## Lab Report - April 2023
s | [18 empty] | s | [16 empty] | s | [13 empty] | s | [12 empty] | s | [10 empty] | s | [14 empty] | s
KATHMANDU, NEPAL | [18 empty] | KATHMANDU, NEPAL | [16 empty] | KATHMANDU, NEPAL | [13 empty] | KATHMANDU, NEPAL | [12 empty] | KATHMANDU, NEPAL | [10 empty] | KATHMANDU, NEPAL | [14 empty] | KATHMANDU, NEPAL
Project No: | 10M170 | [13 empty] | Month: | 2023-04-01 |  |  | Project No: | 10M170 | [10 empty] | Month: |  |  | 2023-04-01 |  | Project No: | 10M170 | [8 empty] | Month: | 2023-04-01 |  |  | Project No: |  | 10M170 | [6 empty] | Month: | 2023-04-01 |  |  | Project No: | 10M170 | [6 empty] | Month: | 2023-04-01 |  | Project No: |  | 10M170 | [7 empty] | Month: | 2023-04-01 |  |  |  | Project No: | 10M170 | [9 empty] | Month: | 2023-04-01
Date | Power Generation and Consumption |  |  |  | Inlet | [13 empty] | Date | Grit Classifier Outlet | Primary Clarifier |  |  |  |  | Secondary Clarifier |  |  |  |  | Secondary Sedimentation tank Outlet |  |  |  |  | Date | CHLORINE CONTACT TANK (Composite) | [5 empty] | CHLORINE CONTACT TANK | [6 empty] | Aeration Tank | [12 empty] | Digester Sludge Feeding Details | [10 empty] | Digester Performance Details | [14 empty] | Digester Outlet |  |  |  | Centrifuge |  |  | Bio Gas |  |  | Scrubber |  | Odour Control Unit
| Power Generation from Gas Engine | Daily Power Consumption from NEA (MW) | Total Power Consumption from NEA & GE (MW) | Total Power (KWh)/Flow (ML) | Raw Sewage Flow | Raw Sewage (Composite) | [5 empty] | Raw Sewage | [37 empty] | DATE | Existing Aeration Tank | [5 empty] | New Aeration Tank | [5 empty] | DATE | Primary sedimentation tank Underflow |  |  | Thickener Sludge Parameters | [6 empty] | DATE | Digester - A | [6 empty] | Digester - B | [6 empty] | DATE | Centrifuge Feed |  |  | Centrifuge Cake |  | Centrifuge Feed Totalizer | Gas Generation | Methane | Carbon Dioxide | Inlet | Outlet
[6 empty] | pH | BOD5 | COD | TSS | NH3-N | O & G | pH | BOD5 | COD | TSS | PO4 | Total Coliform | Fecal coliform |  | TSS | PH | TSS | BOD5 | COD | PST Sludge Totalizer | PH | TSS | BOD5 | COD | Existing RAS | PH | TSS | BOD5 | COD | New RAS |  | pH | BOD5 | COD | TSS | O & G | Ammonical Nitrogen | pH | BOD5 | COD | TSS | Total Coliform | Fecal coliform | FRC |  | PH | DO | MLSS | MLVSS | SV30 | SVI | PH | DO | MLSS | MLVSS | SV30 | SVI |  | pH | TS | VS | pH | TS | VS | VFA | Alkalinity | VFA/ Alkalinity Ratio | Digester Feed Totalizer |  | pH | TS | VS | VFA - mg/l | Alkalinity | VFA/ Alkalinity Ratio | Temp | pH | TS | VS | VFA - mg/l | Alkalinity | VFA/ Alkalinity Ratio | Temp |  | PH | TS | VS | TS | VS |  |  | CH4 | CO2 | H2S | H2S | Inlet pH | Outlet pH
Control Limits |  |  |  |  | 32.4 | 6.0 - 9.0 | 300 | 800 | 400 | 79 | 120 | 6.0 - 9.0 | 300 | 800 | 400 | 12 | 107-109 | 106-107 | Control Limits | - | [15 empty] | Control Limits | 6.5-8.0 | < 10 | < 250 | < 10 | < 10 | < 50 | 6.5-8.0 | < 10 | < 250 | < 10 | < 500 | < 100 | Max 1 | Control Limits | - | > 0.5 | - | - | - | - | - | > 0.5 | - | - | - | - | Control Limits | [10 empty] | Control Limits | [14 empty] | Control Limits
Units | MW | <482.02 KWh / ML of Treated Water |  |  | MLD | - | mg/L | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Units | mg/L | - | mg/L | mg/L | mg/L | m3 | - | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | mg/L | Units | - | mg/L | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | MPN /100ml | MPN /100ml | mg/L | Units | - | mg/L | mg/L | mg/L | ml/L | - | - | mg/L | mg/L | mg/L | ml/L | - | Units | - | % | % | - | % | % | mg/l | mg/l | - | m3 | Units | - | % | % | mg/l | mg/l | - | 0C | - | % | % | mg/l | mg/l | - | 0C | Units | - | % | % | % | % | m3 | Nm3 | % | % | ppm | ppm | - | -
2023-04-01 | 1.6 | 14.76 | 16.36 | 764.6289 | 21.396 | 7.05 | 419.6 | 649 | 445 | 58.2 | 45.5 | 7.1 | 479.1 | 919 | 490 | - | 210000000 | 30000000 | 2023-04-01 | 550 | 7.09 | 1105 | 689.1 | 977 | 421 | 7.01 | 18 | 15.1 | 74 | 10520 | 6.8 | 20 | 18.1 | 101 | 8780 | 2023-04-01 | 7.25 | 18.2 | 51 | 31.6 | 7.5 | 18.2 | 6.98 | 12.9 | 52 | 14.3 | 720 | 360 | 0.2 | 2023-04-01 | 6.87 | 0.655 | 6740 | 4365 | 950 | 141.2939 | 6.72 | 0.975 | 4515 | 3315 | 540 | 120.3416 | 2023-04-01 | 6.7175 | 3.59 | 56.515 | 6.71 | 3.59 | 50.43 | - | 475 | - | 170 | 2023-04-01 | 7.29 | 4.21 | 53.51 | 1800 | 1512 | 1.1905 | 29 | 7.25 | 3.83 | 52.13 | 1575 | 1380 | 1.1413 | 28 | 2023-04-01 | 7.2 | 3.35 | 51.03 | 20.78 | 52.34 | 183 | - | - | - | - | - | - | -
2023-04-02 | 1.6 | 10.97 | 12.57 | 787.6927 | 15.958 | 7.38 | 568.9 | 669 | 645 | 67.2 | 40.5 | 7.27 | 599.6 | 759 | 655 | - | 58000000 | 24000000 | 2023-04-02 | 635 | 7.18 | 955 | 359.6 | 957 | 251 | 6.71 | 29 | 16.6 | 39 | 7490 | 6.14 | 21 | 14.6 | 36 | 7900 | 2023-04-02 | - | - | 142 | 58 | 9 | 16.5 | 7.09 | 13.4 | 50 | 21.6 | 800 | 400 | 0.5 | 2023-04-02 | 6.8 | 0.58 | 6825 | 3990 | 940 | 137.7556 | 6.755 | 0.9 | 4635 | 2705 | 415 | 89.8384 | 2023-04-02 | 6.5675 | 3.4375 | 57.775 | 6.42 | 3.61 | 59.37 | 972 | 475 | 2.0463 | 170 | 2023-04-02 | 7.13 | 4.22 | 48.92 | 1200 | 1775 | 0.67606 | 29 | 6.91 | 4.6 | 51.83 | 1128 | 1350 | 0.83556 | 28 | 2023-04-02 | 7.03 | 3.73 | 45.63 | 20.93 | 51.45 | 151 | - | - | - | - | - | 5.4 | 2.01
2023-04-03 | 1.5 | 11.57 | 13.07 | 701.632 | 18.628 | 7.03 | 389.6 | 744 | 460 | 69.4 | 56 | 7.46 | 418.9 | 907 | 430 | - | - | - | 2023-04-03 | 415 | 7.29 | 645 | 508.9 | 783 | 325 | 7.18 | 23 | 17.9 | 31 | 10430 | 7.2 | 17 | 14.9 | 43 | 6640 | 2023-04-03 | 7.32 | 27.6 | 113 | 61.3 | 7 | 44.8 | 6.94 | 9.1 | 28 | 11 | - | - | 0.2 | 2023-04-03 | 6.76 | 0.565 | 6800 | 4375 | 930 | 136.7829 | 6.74 | 0.93 | 4735 | 2670 | 360 | 75.7326 | 2023-04-03 | 6.7 | 3.435 | 56.5725 | 6.62 | 5.36 | 57.12 | - | 250 | - | 89 | 2023-04-03 | 7.24 | 4.67 | 36.24 | 1300 | 1875 | 0.69333 | 28 | 7.09 | 5.27 | 71.87 | 1908 | 1450 | 1.3159 | 26 | 2023-04-03 | 7.18 | 3.91 | 47.46 | 20.53 | 53.3 | 177 | - | - | - | - | - | - | -
2023-04-04 | 1.5 | 13.3 | 14.8 | 799.3519 | 18.515 | 7.17 | 329.7 | 759 | 405 | 64.4 | 58.5 | 7.24 | 419.6 | 962 | 555 | - | 23000000 | 19000000 | 2023-04-04 | 510 | 7.17 | 1595 | 509.6 | 858 | 334 | 6.81 | 18 | 16.6 | 48 | 10370 | 6.8 | 17 | 15.6 | 57 | 9400 | 2023-04-04 | 7.19 | 20.7 | 74 | 32.7 | 6.5 | 17.6 | 7.21 | 21.6 | 60 | 26 | 520 | 90 | 0.2 | 2023-04-04 | 6.85 | 0.66 | 6745 | - | 950 | 141.1028 | 6.685 | 0.89 | 4675 | - | 390 | 83.4683 | 2023-04-04 | 6.71 | 3.14 | 61.01 | 6.69 | 5.17 | 59.52 | 840 | 375 | 2.24 | 62 | 2023-04-04 | 7.2 | 3.41 | 49.48 | 1332 | 1825 | 0.72986 | 28 | 7.04 | 4.55 | 50.3 | - | 1550 | - | 26 | 2023-04-04 | 7.07 | 3.63 | 53.18 | 20.72 | - | 161 | - | - | - | - | - | 6.9 | 2.55
2023-04-05 | 1.1 | 14.41 | 15.51 | 820.4179 | 18.905 | 7.2 | 389.8 | 907 | 510 | 62.7 | 61 | 7.11 | 359.7 | 783 | 415 | - | 51000000 | 20000000 | 2023-04-05 | - | 7 | 1735 | 389.7 | 907 | 304 | 6.74 | 22 | 17.7 | 52 | 9830 | 6.79 | 19 | 14.7 | 51 | 8170 | 2023-04-05 | 6.9 | 17.8 | 96 | 37 | 8 | 15.4 | - | - | - | - | - | - | 0.2 | 2023-04-05 | 6.7 | 0.66 | 6595 | - | 930 | 141.0283 | 6.66 | 0.925 | 4275 | - | 490 | 113.7205 | 2023-04-05 | 6.6 | 3.31 | 53.1175 | 6.41 | 4.9 | 54.09 | 948 | 400 | 2.37 | 98 | 2023-04-05 | 7.13 | 5.95 | 45.3 | 1548 | 1900 | 0.81474 | 28 | 7.01 | 4.83 | 48.07 | 1608 | 1775 | 0.90592 | 26 | 2023-04-05 | - | - | - | - | - | 109 | - | - | - | - | - | - | -
2023-04-06 | 1.8 | 12.46 | 14.26 | 811.7031 | 17.568 | 7.33 | 509.3 | 979 | 625 | 63.8 | 54 | 7.44 | 419.8 | 977 | 625 | - | 43000000 | 23000000 | 2023-04-06 | 545 | 7.27 | 1300 | 479.8 | 1020 | 404 | 7.01 | 28 | 15.8 | 69 | 10200 | 6.6 | 17 | 14.8 | 74 | 7340 | 2023-04-06 | 7.11 | 26.3 | 77 | 55 | 7.5 | 20.7 | 6.8 | 14.8 | 89 | 16.5 | 340 | 130 | 0.2 | 2023-04-06 | 7.005 | 0.72 | 6735 | 4510 | 945 | 140.4691 | 6.665 | 0.86 | 4765 | 3220 | 360 | 75.6369 | 2023-04-06 | 6.6575 | 3.145 | 56.1875 | 6.9 | 5.3 | 55.99 | 792 | 375 | 2.112 | 79 | 2023-04-06 | 7.4 | 4.83 | 47.66 | 1452 | 1950 | 0.74462 | 28 | 7.18 | 4.82 | 56.22 | 1668 | 1650 | 1.0109 | 27 | 2023-04-06 | 7.39 | 4.05 | 42.38 | 20.42 | 58.31 | 147 | - | - | - | 453 | 113 | 7 | 2.95
2023-04-07 | 1.5 | 15.2 | 16.7 | 960.2668 | 17.391 | 7.13 | 449.2 | 755 | 560 | 59.9 | 40 | 7.14 | 479.3 | 754 | 550 | - | 46000000 | - | 2023-04-07 | 625 | 7.11 | 1250 | 569.3 | 977 | 329 | 6.92 | 16 | 14.3 | 67 | 10940 | 6.89 | 18 | 16.3 | 52 | 7040 | 2023-04-07 | 7.07 | 20.2 | 78 | 31 | 4 | 22.1 | 7.64 | 20.3 | 55 | 40.5 | 600 | - | 0.5 | 2023-04-07 | 6.805 | 0.585 | 6520 | 4105 | 945 | 144.9439 | 6.85 | 0.835 | 4910 | 3195 | 390 | 79.4619 | 2023-04-07 | 6.4275 | 3.65 | 45.6 | 6.71 | 4.67 | 57.16 | 1176 | 350 | 3.36 | 83 | 2023-04-07 | 7.24 | 4.99 | 47.4 | 1752 | 1925 | 0.91013 | 28 | 7.14 | 4.88 | 45.81 | 1488 | 1425 | 1.0442 | 27 | 2023-04-07 | - | - | - | - | - | 41 | - | - | - | 566 | 113 | 6.92 | 2.95
2023-04-08 | 1.1 | 14.25 | 15.35 | 790.8295 | 19.41 | 7 | 569.2 | 948 | 635 | 45.4 | 61 | 7.08 | 509.2 | 925 | 620 | - | 39000000 | - | 2023-04-08 | - | 7.04 | 660 | 419.2 | 731 | 312 | 6.88 | 19 | 15.2 | 68 | 9440 | 6.82 | 26 | 16.2 | 66 | 10020 | 2023-04-08 | 6.9 | 28.2 | 89 | 40 | 3.5 | 12.6 | 7.02 | 17.2 | 72 | 22.5 | 360 | - | 0.2 | 2023-04-08 | 6.825 | 0.68 | 7120 | 3675 | 905 | 127.3698 | 6.795 | 0.83 | 4885 | 3620 | 480 | 98.3019 | 2023-04-08 | 6.48 | 4.315 | 50.5075 | 6.74 | 5.57 | - | - | 500 | - | 74 | 2023-04-08 | 7.18 | 4.41 | 44.04 | 1404 | 1950 | 0.72 | 28 | 7.18 | 4.98 | 43.6 | 1584 | 1725 | 0.91826 | 27 | 2023-04-08 | - | - | - | - | - | 62 | - | - | - | 453 | 141 | 6.98 | 2.21
2023-04-09 | 1 | 15.4 | 16.4 | 1124.1346 | 14.589 | 7.06 | 359.6 | 982 | 405 | 52.6 | 50.5 | 7.28 | 479.2 | 1018 | 545 | - | 28000000 | - | 2023-04-09 | - | 7.01 | 715 | 539.2 | 790 | 284 | 6.9 | 19 | 16.2 | 60 | 9350 | 6.71 | 25 | 19.2 | 96 | 9060 | 2023-04-09 | 7.1 | 30.6 | 78 | 48 | 4.5 | 9.5 | 6.71 | 15.2 | 55 | 17 | 420 | - | 0.2 | 2023-04-09 | 6.9 | 0.595 | 6240 | 3990 | 960 | 155.7506 | 6.735 | 0.655 | 5505 | 3760 | 875 | 159.1789 | 2023-04-09 | 6.6 | 3.8625 | 50.4625 | 6.71 | 5.35 | 54.91 | 984 | 275 | 3.5782 | 67 | 2023-04-09 | 7.09 | 4.34 | 42.38 | 1116 | 2075 | 0.53783 | 28 | 6.93 | 5.11 | 44.99 | 2160 | 1500 | 1.44 | 27 | 2023-04-09 | 7 | 3.9706 | 49.5441 | 21.2 | 53.52 | 166 | - | - | - | - | - | 7.06 | 2.98
2023-04-10 | 1.1 | 15.38 | 16.48 | 949.6917 | 17.353 | 7 | 539.1 | 943 | 625 | 56 | 40.5 | 7.12 | 539.6 | 1023 | 735 | - | 41000000 | - | 2023-04-10 | 335 | 7.08 | 500 | 419.6 | 747 | 302 | 6.93 | 18 | 15.6 | 64 | 9650 | 6.78 | 16 | 13.6 | 52 | 12030 | 2023-04-10 | 7.25 | 25.1 | 74 | 37 | 8.5 | 33.6 | 7.06 | 17.6 | 68 | 20 | 530 | - | 0.2 | 2023-04-10 | 6.9 | 0.54 | 6570 | 4255 | 955 | 146.3936 | 6.785 | 0.435 | 5790 | 3850 | 875 | 151.087 | 2023-04-10 | 6.59 | 3.3125 | 56.6525 | 6.79 | 4.03 | 68.78 | - | 325 | - | 68 | 2023-04-10 | 7.09 | 3.66 | 50.66 | - | 1925 | - | 28 | 6.98 | 4.21 | 46.57 | - | 1750 | - | 27 | 2023-04-10 | 6.91 | 3.8849 | 46.6346 | 20.47 | 53.84 | 69 | - | - | - | - | - | - | -
2023-04-11 | 1.1 | 16.11 | 17.21 | 873.6484 | 19.699 | 7.09 | 419.4 | 882 | 570 | 61.6 | 52 | 7.18 | 479.1 | 994 | 565 | - | 54000000 | - | 2023-04-11 | 750 | 7.05 | 640 | 449.1 | 892 | 340 | 6.9 | 16 | 14.1 | 84 | 12060 | 6.76 | 15 | 12.1 | 89 | 9780 | 2023-04-11 | 7.3 | 23.4 | 55 | 16.4 | 6 | 7.3 | 6.9 | 13.1 | 52 | 16.8 | 560 | - | 0.5 | 2023-04-11 | 7.13 | 0.455 | 5870 | 3735 | 950 | 161.8661 | 6.97 | 0.57 | 5815 | 4180 | 900 | 154.9058 | 2023-04-11 | 6.6575 | 2.935 | 54.78 | 6.67 | 4.96 | 56.03 | - | 400 | - | 58 | 2023-04-11 | 7.17 | 4.04 | 46.01 | - | 2025 | - | 28 | 7.03 | 4.24 | 49.48 | - | 1450 | - | 27 | 2023-04-11 | 6.88 | 3.9978 | 50.5155 | 21.6 | 42.51 | 39 | - | - | - | - | - | 6.92 | 4.1
2023-04-12 | 1.4 | 13.06 | 14.46 | 859.2821 | 16.828 | 7.27 | 509.4 | 982 | 620 | 82.9 | 84 | 7.21 | 479.4 | 943 | 585 | - | 44000000 | - | 2023-04-12 | 475 | 7.06 | 620 | 389.4 | 749 | 312 | 6.83 | 17 | 15.4 | 79 | 11910 | 6.79 | 16 | 14.4 | 89 | 10670 | 2023-04-12 | 7.19 | 18.4 | 69 | 24 | 4 | 28.3 | 7.06 | 15.4 | 69 | 31 | 200 | - | 1 | 2023-04-12 | 7.07 | 0.48 | 6580 | 4185 | 950 | 144.6388 | 6.905 | 0.555 | 5930 | 3985 | 910 | 153.6404 | 2023-04-12 | 6.655 | 3.3725 | 50.5575 | 6.34 | 5.37 | 52.67 | 1440 | 375 | 3.84 | 111 | 2023-04-12 | 7.14 | 4.38 | 43.88 | 3312 | 1925 | 1.7205 | 28 | 6.89 | 4.98 | 43.67 | 2604 | 1500 | 1.736 | 27 | 2023-04-12 | - | - | - | - | - | 0 | - | - | - | - | - | 7.18 | 2.37
2023-04-13 | 1.3 | 12.99 | 14.29 | 796.2777 | 17.946 | 7.08 | 509.2 | 868 | 550 | 68.9 | 55.5 | 7.19 | 479.4 | 948 | 590 | - | 37000000 | - | 2023-04-13 | - | 7.05 | 675 | 449.4 | 731 | 315 | 6.81 | 15 | 13.4 | 66 | 10030 | 6.94 | 17 | 14.4 | 68 | 12060 | 2023-04-13 | 7.29 | 20.2 | 55 | 24 | 7 | 6.2 | 7 | 12.4 | 66 | 13.2 | 380 | - | 0.5 | 2023-04-13 | 6.945 | 0.48 | 6325 | 3920 | 945 | 150.3901 | 6.85 | 0.495 | 6115 | 3275 | 970 | 159.2164 | 2023-04-13 | 6.41 | 3.28 | 47.3975 | 6.36 | 4.58 | 57.86 | 1176 | 450 | 2.6133 | 90 | 2023-04-13 | 7.15 | 3.94 | 45.37 | 2400 | 1900 | 1.2632 | 28 | 7.02 | 5.25 | 47.04 | 2292 | 1650 | 1.3891 | 27 | 2023-04-13 | 6.94 | 4.5307 | 50.6726 | 20.42 | 52.44 | 87 | - | - | - | - | - | - | -
2023-04-14 | 1.3 | 12.95 | 14.25 | 848.1133 | 16.802 | 7.23 | 629.2 | 834 | 655 | 53.8 | 83 | - | - | - | - | - | 28000000 | - | 2023-04-14 | - | - | - | - | - | 214 | - | - | - | - | - | - | - | - | - | - | 2023-04-14 | 7.28 | 19.2 | 60 | 24 | 6.5 | 9.5 | - | - | - | - | 440 | - | - | 2023-04-14 | - | - | - | - | - | - | - | - | - | - | - | - | 2023-04-14 | - | - | - | - | - | - | - | - | - | 170 | 2023-04-14 | - | - | - | - | - | - | 28 | - | - | - | - | - | - | 27 | 2023-04-14 | - | - | - | - | - | 57 | - | - | - | - | - | - | -
2023-04-15 | 1.4 | 13.88 | 15.28 | 926.229 | 16.497 | 6.93 | 749.2 | 1032 | 836 | 64.4 | 60.5 | 7.01 | 509.2 | 989 | 580 | - | 48000000 | - | 2023-04-15 | 535 | 7.03 | 945 | 599.2 | 848 | 247 | 6.8 | 19 | 15.2 | 67 | 11190 | 6.91 | 18 | 13.2 | 96 | 11960 | 2023-04-15 | 7.11 | 21.2 | 62 | 27.5 | 7 | 9.8 | 7.06 | 18.2 | 48 | 21.6 | 510 | - | 0.2 | 2023-04-15 | 6.995 | 0.51 | 6860 | 3815 | 965 | 141.0207 | 6.89 | 0.445 | 6045 | 3430 | 925 | 153.154 | 2023-04-15 | 6.72 | 3.335 | 49.4875 | 6.62 | 5 | 52.23 | - | 475 | - | 100 | 2023-04-15 | 7.25 | 3.95 | 42 | 3144 | 1825 | 1.7227 | 28 | 7.02 | 4.65 | 45.92 | 2856 | 1300 | 2.1969 | 27 | 2023-04-15 | - | - | - | - | - | 40 | - | - | - | - | - | - | -
2023-04-16 | 1.3 | 13.43 | 14.73 | 1004.6378 | 14.662 | 7.2 | 449.4 | 940 | 505 | 67.2 | 43 | 7.22 | 629.2 | 972 | 635 | - | 32000000 | - | 2023-04-16 | 250 | 6.91 | 3155 | 839.2 | 894 | 269 | 7.05 | 20 | 15.2 | 74 | 11450 | 6.89 | 14 | 12.2 | 86 | 12560 | 2023-04-16 | 7.01 | 13.4 | 91 | 19 | 7 | 11.8 | 6.91 | 15.2 | 55 | 19 | 540 | - | 0.5 | 2023-04-16 | 6.805 | 0.32 | 7710 | 4920 | 960 | 124.9584 | 6.825 | 0.515 | 6715 | 4400 | 935 | 139.4871 | 2023-04-16 | 6.435 | 3.22 | 45.42 | 6.71 | 4.06 | 49.05 | - | 375 | - | 122 | 2023-04-16 | 7.18 | 3.69 | 40.6 | 1440 | 2025 | 0.71111 | 28 | 7.2 | 4.36 | 41.97 | 2610 | 1500 | 1.74 | 27 | 2023-04-16 | 7.15 | 4.11 | 31.1 | 20.31 | 56.5 | 169 | - | - | - | - | - | 7.28 | 2.01
2023-04-17 | 1.4 | 14.06 | 15.46 | 923.5916 | 16.739 | 7.23 | 479.1 | 887 | 535 | 53.8 | 61.5 | 7.18 | 479.4 | 1027 | 595 | - | 39000000 | - | 2023-04-17 | 530 | 7 | 1400 | 629.4 | 960 | 313 | 6.94 | 17 | 13.4 | 96 | 11350 | 6.84 | 19 | 14.4 | 106 | 12430 | 2023-04-17 | 7.2 | 18.1 | 43 | 23.5 | 5.5 | 18.2 | 6.94 | 10.4 | 84 | 13 | 360 | - | 0.2 | 2023-04-17 | 6.87 | 0.395 | 7860 | 5050 | 965 | 123.091 | 6.875 | 0.4 | 6930 | 4510 | 965 | 139.3393 | 2023-04-17 | 6.6975 | 3.4825 | 41.2475 | 6.55 | 5.15 | 49.01 | - | 425 | - | 139 | 2023-04-17 | 7.09 | 4.37 | 42.43 | 2520 | 1925 | 1.3091 | 28 | 7.09 | 4.82 | 38.2 | 2298 | 1675 | 1.3719 | 27 | 2023-04-17 | 7 | 3.98 | 43.41 | 20.74 | 55.38 | 162 | - | - | - | - | - | 7.28 | 2.24
2023-04-18 | 1.4 | 12.01 | 13.41 | 695.792 | 19.273 | 7.23 | 539.7 | 887 | 605 | 52.6 | 78.5 | 7.08 | 539.1 | 1006 | 650 | - | 26000000 | - | 2023-04-18 | 1000 | 7.03 | 1415 | 569.1 | 1027 | 354 | 6.96 | 29 | 18.1 | 67 | 11370 | 6.83 | 18 | 14.1 | 62 | 14780 | 2023-04-18 | 7.3 | 14.7 | 40 | 18.5 | 6 | 9.8 | 7.09 | 16.1 | 38 | 21 | 290 | - | 0.1 | 2023-04-18 | 6.975 | 0.44 | 7600 | 5000 | 960 | 126.5843 | 6.87 | 0.54 | 6555 | 4400 | 750 | 113.6059 | 2023-04-18 | 6.6925 | 2.96 | 50.04 | 6.58 | 3.78 | 50.25 | 1140 | 425 | 2.6824 | 160 | 2023-04-18 | 7.11 | 3.88 | 46.38 | 2778 | 2000 | 1.389 | 28 | 7.07 | 3.87 | 43.85 | 2208 | 2025 | 1.0904 | 27 | 2023-04-18 | 7.06 | 2.98 | 47.45 | 21.69 | - | 164 | - | - | - | 453 | 113 | 7.38 | 2.63
2023-04-19 | 1.6 | 13.71 | 15.31 | 853.3051 | 17.942 | 7.18 | 449.3 | 907 | 560 | 61.6 | 54 | 7.15 | 509.7 | 894 | 550 | - | 30000000 | - | 2023-04-19 | - | 7.06 | 615 | 479.7 | 723 | 330 | 6.99 | 20 | 15.7 | 50 | 11120 | 7.01 | 15 | 13.7 | 64 | 15470 | 2023-04-19 | 7.24 | 8.3 | 69 | 9.5 | 2.5 | 17.9 | 7.18 | 11.7 | 35 | 13.5 | 520 | - | 0.1 | 2023-04-19 | 6.98 | 0.44 | 7555 | 4730 | 950 | 126.0198 | 6.93 | 0.545 | 6945 | 4245 | 770 | 110.1015 | 2023-04-19 | 6.6675 | 3.99 | 46.82 | 6.69 | 4.01 | 55.22 | 1104 | 450 | 2.4533 | 170 | 2023-04-19 | 7.18 | 4.59 | 40.19 | 2334 | 2025 | 1.1526 | 29 | 7.12 | 4.08 | 40.92 | 2400 | 1900 | 1.2632 | 27 | 2023-04-19 | 7 | 3.76 | 45.67 | 21.09 | 52.13 | 171 | - | - | - | 566 | 113 | 7.4 | 1.97
2023-04-20 | 1.5 | 13.48 | 14.98 | 850.4116 | 17.615 | 6.98 | 389.1 | 754 | 400 | 59.4 | 67.5 | 7.22 | 419.3 | 962 | 575 | - | 33000000 | - | 2023-04-20 | - | 7.04 | 785 | 494.3 | 727 | 324 | 6.96 | 18 | 16.3 | 84 | 12160 | 6.94 | 19 | 15.3 | 77 | 14060 | 2023-04-20 | 7.53 | 13.1 | 28 | 15 | 6 | 12.3 | 7.08 | 10.3 | 72 | 12 | 590 | - | 0.2 | 2023-04-20 | 6.895 | 0.445 | 7290 | 4065 | 965 | 133.3094 | 6.925 | 0.55 | 6930 | 3765 | 870 | 125.638 | 2023-04-20 | 6.625 | 3.1925 | 56.2225 | 6.66 | 4.07 | 59.93 | 1044 | 500 | 2.088 | 170 | 2023-04-20 | 7.19 | 3.89 | 52.26 | 2304 | 2025 | 1.1378 | 29 | 7.15 | 4.19 | 49.09 | 2094 | 2075 | 1.0092 | 27 | 2023-04-20 | 7.16 | 3.46 | 50.36 | 21.83 | 54.88 | 170 | - | - | - | 453 | 141 | 7.19 | 2.3
2023-04-21 | 1.2 | 9.89 | 11.09 | 694.0359 | 15.979 | 7.11 | 523.9 | 886 | 540 | 78.4 | 72 | 6.86 | 464.1 | 887 | 490 | - | 29000000 | - | 2023-04-21 | 410 | 6.86 | 1350 | 509.1 | 914 | 328 | 7.21 | 17 | 14.1 | 52 | 12940 | 7.24 | 20 | 17.1 | 55 | 14770 | 2023-04-21 | 7.21 | 12.9 | 76 | 20 | 7.5 | 25.2 | 7.38 | 10.1 | 45 | 11 | 310 | - | 0.2 | 2023-04-21 | 6.925 | 0.495 | 7995 | 4970 | 970 | 122.2174 | 6.89 | 0.55 | 7460 | 3825 | 945 | 126.8803 | 2023-04-21 | 6.6625 | 2.8525 | 51.3175 | 6.63 | 4.01 | 56.33 | 996 | 475 | 2.0968 | 304 | 2023-04-21 | 7.08 | 4.26 | 51.15 | 2544 | 1975 | 1.2881 | 29 | 6.93 | 3.74 | 46.98 | 2412 | 1925 | 1.253 | 27 | 2023-04-21 | 6.87 | 4.08 | 48.21 | 20.2726 | 55.7471 | 104 | - | - | - | 566 | 141 | 7.32 | 2.06
2023-04-22 | 2.1 | 8.11 | 10.21 | 576.8687 | 17.699 | 7.21 | 569.2 | 965 | 695 | 65 | 76 | 7.04 | 493.9 | 984 | 560 | - | 40000000 | - | 2023-04-22 | - | 6.96 | 735 | 523.9 | 893 | 305 | 7 | 17 | 14.9 | 77 | 13290 | 7.06 | 16 | 14.9 | 84 | 14900 | 2023-04-22 | 7.26 | 14.2 | 50 | 15 | 5.5 | 12.9 | 7.18 | 9.9 | 64 | 16 | 620 | - | 0.5 | 2023-04-22 | 6.865 | 0.455 | 7900 | 4185 | 965 | 122.1635 | 6.96 | 0.46 | 7420 | 3735 | 950 | 128.2127 | 2023-04-22 | 6.8025 | 2.995 | 58.8175 | 7.04 | 2.44 | 49.39 | - | 625 | - | 305 | 2023-04-22 | 7.22 | 4.44 | 52.02 | 2280 | 1975 | 1.1544 | 29 | 7.24 | 3.59 | 51.78 | 2400 | 1925 | 1.2468 | 27 | 2023-04-22 | - | - | - | - | - | 84 | - | - | - | 283 | 170 | - | -
2023-04-23 | 1.9 | 10.21 | 12.11 | 775.4867 | 15.616 | 6.86 | 479 | 894 | 525 | 66.1 | 72 | 7.16 | 404.2 | 827 | 475 | - | 200000000 | - | 2023-04-23 | 695 | 7.02 | 1385 | 599.2 | 943 | 340 | 7.08 | 17 | 14.2 | 64 | 11660 | 7.02 | - | 15.2 |  | 14210 | 2023-04-23 | 7.21 | 21 | 52 | 27.5 | 4.5 | 23.2 | 7.11 | 12.2 | 48 | 13 | 710 | - | 0.2 | 2023-04-23 | 6.97 | 0.44 | 8055 | 5190 | 960 | 119.7699 | 6.895 | 0.62 | 7395 | 4900 | 940 | 127.2598 | 2023-04-23 | 6.685 | 3.0975 | 54.8475 | 6.66 | 3.4 | 56.03 | 912 | 375 | 2.432 | 250 | 2023-04-23 | 7.12 | 5.41 | 49.13 | 2502 | 1825 | 1.371 | 29 | 7.06 | 3.93 | 49.58 | 2346 | 1725 | 1.36 | 27 | 2023-04-23 | 7.03 | 3.35 | 49.74 | 20.31 | 53.62 | 168 | - | - | - | 453 | 141 | - | -
2023-04-24 | 1.9 | 11.07 | 12.97 | 766.5485 | 16.92 | 7.13 | 359.8 | 599 | 465 | 47 | 55 | 7.2 | 359 | 747 | 375 | - | 39000000 | - | 2023-04-24 | 490 | 6.86 | 740 | 494 | 730 | 366 | 6.94 | 24 | 18 | 77 | 11960 | - | - | 18 | - | 15440 | 2023-04-24 | CCT was not in operational .Hence SST and SC sample is taken for analysis. | [12 empty] | 2023-04-24 | 6.905 | 0.385 | 7660 | 5365 | 965 | 126.2732 | 6.85 | 0.665 | 6295 | 4400 | 900 | 143.0182 | 2023-04-24 | 6.4725 | 3.765 | 53.36 | 6.47 | 3.19 | 52.65 | 978 | 325 | 3.0092 | 312 | 2023-04-24 | 6.83 | 3.64 | 51.75 | 2772 | 1925 | 1.44 | 28 | 6.85 | 3.83 | 53.19 | 2394 | 1750 | 1.368 | 26 | 2023-04-24 | 6.72 | 3.92 | 49.89 | 20.19 | 54.94 | 168 | - | - | - | - | - | - | -
2023-04-25 | 1.5 | 11.6 | 13.1 | 724.5174 | 18.081 | 7.23 | 449.1 | 948 | 650 | 56.6 | 54.5 | 7.21 | 314.8 | 899 | 370 | - | 41000000 | - | 2023-04-25 | 580 | 7 | 915 | 494.8 | 945 | 289 | 6.79 | 17 | 13 | 31 | 13110 | - | - | - | - | 10000 | 2023-04-25 | [13 empty] | 2023-04-25 | 6.795 | 0.385 | 7035 | 3415 | 955 | 136.5737 | 6.775 | 0.86 | 5180 | 2570 | 795 | 153.8382 | 2023-04-25 | 6.5025 | 3.6 | 54.5275 | 6.52 | 3.92 | 52.81 | 804 | 375 | 2.144 | 150 | 2023-04-25 | 6.96 | 3.72 | 50.1 | 2934 | 1975 | 1.4856 | 28 | 6.87 | 4.17 | 46.84 | 2640 | 1775 | 1.4873 | 25 | 2023-04-25 | 6.86 | 4.04 | 42.82 | 20.71 | 53.31 | 151 | - | - | - | 566 | 113 | 7.06 | 2.11
2023-04-26 | 1.5 | 14.29 | 15.79 | 857.4066 | 18.416 | 7.04 | 404.6 | 858 | 550 | 58.2 | 77.5 | 7.15 | 419.1 | 914 | 520 | - | 200000000 | - | 2023-04-26 | 605 | 7.01 | 1115 | 554.1 | 1081 | 294 | 6.73 | 17 | 14.7 | 40 | 11040 | - | 285 | - | - | 10660 | 2023-04-26 | [13 empty] | 2023-04-26 | 6.8 | 0.485 | 7570 | 4465 | 940 | 124.7148 | 6.825 | 0.71 | 5220 | 3382.5 | 730 | 139.7678 | 2023-04-26 | 6.5225 | 3.4275 | 54.59 | 6.53 | 3.23 | 48.17 | 906 | 425 | 2.1318 | 167 | 2023-04-26 | 7 | 4.13 | 43.91 | 2598 | 2025 | 1.283 | 28 | 6.86 | 3.96 | 43.24 | 2526 | 1800 | 1.4033 | 25 | 2023-04-26 | 6.9 | 3.13 | 42.95 | 22.6 | 42.2 | 177 | - | - | - | - | - | 7.02 | 2.77
2023-04-27 | 1.5 | 13.03 | 14.53 | 747.8896 | 19.428 | 7.01 | 344.7 | 900 | 375 | 72.2 | 62 | 7.11 | 449.6 | 1037 | 655 | - | 300000000 | - | 2023-04-27 | 1865 | 6.99 | 200 | 194.6 | 452 | 164 | 6.79 | 14 | 12.8 | 19 | 11170 | - | 156 | - | - | 9500 | 2023-04-27 | [13 empty] | 2023-04-27 | 6.81 | 0.465 | 7510 | 4920 | 935 | 125.189 | 6.73 | 0.91 | 3475 | 1940 | 280 | 81.6242 | 2023-04-27 | 6.5575 | 3.4175 | 53.56 | 6.68 | 3.32 | 54.42 | 900 | 400 | 2.25 | 123 | 2023-04-27 | 7.28 | 3.19 | 47.93 | 2322 | 2000 | 1.161 | 28 | 7.01 | 3.79 | 47.29 | 2508 | 1775 | 1.413 | 25 | 2023-04-27 | 7.21 | 3.85 | 49.65 | 20.34 | 46.44 | 167 | - | - | - | 453 | 113 | 6.97 | 2.19
2023-04-28 | 1.4 | 13.39 | 14.79 | 744.3007 | 19.871 | 7.1 | 374.4 | 933 | 440 | 56.6 | 62.5 | 6.88 | 374.7 | 940 | 410 | - | 44000000 | - | 2023-04-28 | - | 6.86 | 1370 | 449.7 | 658 | 518 | 6.8 | 20 | 14.7 | 33 | 9910 | - | 108 | - | - | 10880 | 2023-04-28 | [13 empty] | 2023-04-28 | 6.735 | 0.52 | 7820 | 4235 | 955 | 122.1219 | 6.745 | 0.855 | 4005 | 2175 | 335 | 83.67 | 2023-04-28 | 6.54 | 3.0225 | 55.13 | 6.66 | 3.55 | 54.32 | - | 475 | - | 185 | 2023-04-28 | 7.25 | 3.43 | 50.05 | 2640 | 1925 | 1.3714 | 28 | 7.04 | 3.6 | 49.72 | 2460 | 1700 | 1.4471 | 25 | 2023-04-28 | 7.24 | 3.34 | - | 21.94 | 55.8 | 169 | - | - | - | - | - | 6.91 | 2.01
2023-04-29 | 1.9 | 10.95 | 12.85 | 776.1537 | 16.556 | 6.98 | 479 | - | 595 | 61.6 | - | 7.06 | 404.4 | 894 | 515 | - | 60000000 | - | 2023-04-29 | 555 | 6.93 | 290 | 269.4 | 972 | 164 | 6.89 | 20 | 15.6 | 64 | 11270 | 6.76 | 580 | - | - | 12920 | 2023-04-29 | [13 empty] | 2023-04-29 | 6.8 | 0.48 | 7475 | 4610 | 935 | 125.231 | 6.785 | 0.725 | 5090 | 3305 | 485 | 95.4363 | 2023-04-29 | 6.5725 | 3.57 | 56.12 | 6.69 | 3.36 | 55.83 | - | 400 | - | 168 | 2023-04-29 | 7.22 | 4.54 | 52.99 | 2376 | 1875 | 1.2672 | 28 | 7.07 | 3.63 | 43.28 | 2766 | 1525 | 1.8138 | 25 | 2023-04-29 | 7.2 | 3.64 | 49.72 | 22.05 | 56.87 | 159 | - | - | - | - | - | - | -
2023-04-30 | 1.5 | 12.75 | 14.25 | 774.0359 | 18.41 | 7.18 | 494.3 | - | 530 | 54.9 | 53.5 | 6.91 | 449 | - | 515 | - | 57000000 | - | 2023-04-30 | 565 | 6.9 | 1260 | 494 | - | 156 | 6.81 | 19 | 15.2 | - | 10080 | 6.76 | 598 |  | - | 12330 | 2023-04-30 | [13 empty] | 2023-04-30 | 6.675 | 0.505 | 7355 | 3665 | 960 | 130.525 | 6.725 | 0.66 | 5040 | 3035 | 775 | 153.7161 | 2023-04-30 | 6.48 | 3.5925 | 58.49 | 6.5 | 3.35 | 56.43 | 840 | 450 | 1.8667 | 170 | 2023-04-30 | 6.91 | 3.5107 | 50.1905 | 1764 | 1800 | 0.98 | 28 | 6.8433 | 3.7145 | 50.5032 | 2004 | 1450 | 1.3821 | 25 | 2023-04-30 | 6.86 | 2.79 | 51.97 | 21.67 | 58.12 | 176 | - | - | - | - | - | - | -
AVG | 1.4633 | 12.9557 | 14.419 | 819.2961 | 17.6897 | 7.1207 | 470.8333 | 867.5357 | 550.5333 | 61.4133 | 59.7241 | 7.1469 | 460.7103 | 924.6786 | 545.8621 |  | 66206896.5517 | 23200000 | AVG | 615.2381 | 7.0297 | 1036.8966 | 495.3655 | 853.0714 | 306.9333 | 6.9093 | 19.4138 | 15.3448 | 60.5714 | 10941.0345 | 6.845 | 81.1538 | 15.087 | 71.619 | 11233.1034 | AVG | 7.1918 | 19.6727 | 70.5217 | 30.2391 | 6.1304 | 17.5391 | 7.0638 | 14.1476 | 57.381 | 18.5952 | 491.4286 | 245 | 0.30909 | AVG | 6.8745 | 0.51103 | 7135 | 4359.4444 | 950.3448 | 134.4672 | 6.8141 | 0.685 | 5629.3103 | 3547.8704 | 700.1724 | 121.6993 | AVG | 6.6003 | 3.3898 | 53.0046 | 6.6297 | 4.2172 | 54.8571 | 997.3333 | 413.7931 | 2.5174 | 146.1333 | AVG | 7.149 | 4.1962 | 47.0321 | 2143.2593 | 1920.2414 | 1.1194 | 28.2333 | 7.037 | 4.3267 | 48.0667 | 2189.8846 | 1654.4828 | 1.3301 | 26.5333 | AVG | 7.0374 | 3.7167 | 47.2721 | 20.9919 | 53.0308 | 128.2667 |  |  |  | 478.6364 | 128.3636 | 7.0094 | 2.4672
Remarks: | [18 empty] | Remarks: | [30 empty] | Remarks: | [12 empty] | Remarks: | [10 empty] | Remarks: | [14 empty] | Remarks:
*BDL - Below Detectable Limit, ([-] - analysis not conducted) | [18 empty] | *BDL - Below Detectable Limit | [16 empty] | *BDL - Below Detectable Limit | [13 empty] | *BDL - Below Detectable Limit | [12 empty] | *BDL - Below Detectable Limit | [10 empty] | *BDL - Below Detectable Limit | [14 empty] | *BDL - Below Detectable Limit
VA TECH WABAG | [14 empty] | PID | KVWSMB |  |  | VA TECH WABAG | [7 empty] | PID |  |  |  |  | KVWSMB |  |  |  | VA TECH WABAG | [9 empty] | PID | KVWSMB |  |  | VA TECH WABAG |  |  |  |  | PID |  |  |  | KVWSMB |  |  |  | VA TECH WABAG |  |  |  |  | PID |  |  | KVWSMB |  |  | VA TECH WABAG |  |  |  |  | PID |  |  |  |  | KVWSMB |  |  |  |  | VA TECH WABAG | [9 empty] | PID |  | KVWSMB
CHEMIST |  |  |  |  | PLANT INCHARGE | [6 empty] | PLANT INCHARGE | [6 empty] | CHEMIST |  | PLANT INCHARGE | [14 empty] | CHEMIST | [7 empty] | PLANT INCHARGE | [5 empty] | CHEMIST |  | PLANT INCHARGE | [10 empty] | CHEMIST |  | PLANT INCHARGE | [8 empty] | CHEMIST |  | PLANT INCHARGE | [12 empty] | CHEMIST |  |  | PLANT INCHARGE
Formulas:
Date = [Date]
Aeration Tank = [Date]
Digester Sludge Feeding Details = [Aeration Tank]
Digester Performance Details = [Digester Sludge Feeding Details]
Digester Outlet = [Digester Performance Details]