## Lab Report - February 2023
32.4 MLD WWTP, Guheshwori | [18 empty] | 32.4 MLD WWTP, Guheshwori | [16 empty] | 32.4 MLD WWTP, Guheshwori | [13 empty] | 32.4 MLD WWTP, Guheshwori | [12 empty] | 32.4 MLD WWTP, Guheshwori | [10 empty] | 32.4 MLD WWTP, Guheshwori | [14 empty] | 32.4 MLD WWTP, Guheshwori
KATHMANDU, NEPAL | [18 empty] | KATHMANDU, NEPAL | [16 empty] | KATHMANDU, NEPAL | [13 empty] | KATHMANDU, NEPAL | [12 empty] | KATHMANDU, NEPAL | [10 empty] | KATHMANDU, NEPAL | [14 empty] | KATHMANDU, NEPAL
Project No: | 10M170 | [13 empty] | Month: | 2023-02-01 |  |  | Project No: | 10M170 | [10 empty] | Month: |  |  | 2023-02-01 |  | Project No: | 10M170 | [8 empty] | Month: | 2023-02-01 |  |  | Project No: |  | 10M170 | [6 empty] | Month: | 2023-02-01 |  |  | Project No: | 10M170 | [6 empty] | Month: | 2023-02-01 |  | Project No: |  | 10M170 | [7 empty] | Month: | 2023-02-01 |  |  |  | Project No: | 10M170 | [9 empty] | Month: | 2023-02-01
Date | Power Generation and Consumption |  |  |  | Inlet | [13 empty] | Date | Grit Classifier Outlet | Primary Clarifier |  |  |  |  | Secondary Clarifier |  |  |  |  | Secondary Sedimentation tank Outlet |  |  |  |  | Date | CHLORINE CONTACT TANK (Composite) | [5 empty] | CHLORINE CONTACT TANK | [6 empty] | Aeration Tank | [12 empty] | Digester Sludge Feeding Details | [10 empty] | Digester Performance Details | [14 empty] | Digester Outlet |  |  |  | Centrifuge |  |  | Bio Gas |  |  | Scrubber |  | Odour Control Unit
| Power Generation from Gas Engine | Daily Power Consumption from NEA (MW) | Total Power Consumption from NEA & GE (MW) | Total Power (KWh)/Flow (ML) | Raw Sewage Flow | Raw Sewage (Composite) | [5 empty] | Raw Sewage | [37 empty] | DATE | Existing Aeration Tank | [5 empty] | New Aeration Tank | [5 empty] | DATE | Primary sedimentation tank Underflow |  |  | Thickener Sludge Parameters | [6 empty] | DATE | Digester - A | [6 empty] | Digester - B | [6 empty] | DATE | Centrifuge Feed |  |  | Centrifuge Cake |  | Centrifuge Feed Totalizer | Gas Generation | Methane | Carbon Dioxide | Inlet | Outlet
[6 empty] | pH | BOD5 | COD | TSS | NH3-N | O & G | pH | BOD5 | COD | TSS | PO4 | Total Coliform | Fecal coliform |  | TSS | PH | TSS | BOD5 | COD | PST Sludge Totalizer | PH | TSS | BOD5 | COD | Existing RAS | PH | TSS | BOD5 | COD | New RAS |  | pH | BOD5 | COD | TSS | O & G | Ammonical Nitrogen | pH | BOD5 | COD | TSS | Total Coliform | Fecal coliform | FRC |  | PH | DO | MLSS | MLVSS | SV30 | SVI | PH | DO | MLSS | MLVSS | SV30 | SVI |  | pH | TS | VS | pH | TS | VS | VFA | Alkalinity | VFA/ Alkalinity Ratio | Digester Feed Totalizer |  | pH | TS | VS | VFA - mg/l | Alkalinity | VFA/ Alkalinity Ratio | Temp | pH | TS | VS | VFA - mg/l | Alkalinity | VFA/ Alkalinity Ratio | Temp |  | PH | TS | VS | TS | VS |  |  | CH4 | CO2 | H2S | H2S | Inlet pH | Outlet pH
Control Limits |  |  |  |  | 32.4 | 6.0 - 9.0 | 300 | 800 | 400 | 79 | 120 | 6.0 - 9.0 | 300 | 800 | 400 | 12 | 107-109 | 106-107 | Control Limits | - | [15 empty] | Control Limits | 6.5-8.0 | < 10 | < 250 | < 10 | < 10 | < 50 | 6.5-8.0 | < 10 | < 250 | < 10 | < 500 | < 100 | Max 1 | Control Limits | - | > 0.5 | - | - | - | - | - | > 0.5 | - | - | - | - | Control Limits | [10 empty] | Control Limits | [14 empty] | Control Limits
Units | MW | <482.02 KWh / ML of Treated Water |  |  | MLD | - | mg/L | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Units | mg/L | - | mg/L | mg/L | mg/L | m3 | - | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | mg/L | Units | - | mg/L | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | MPN /100ml | MPN /100ml | mg/L | Units | - | mg/L | mg/L | mg/L | ml/L | - | - | mg/L | mg/L | mg/L | ml/L | - | Units | - | % | % | - | % | % | mg/l | mg/l | - | m3 | Units | - | % | % | mg/l | mg/l | - | 0C | - | % | % | mg/l | mg/l | - | 0C | Units | - | % | % | % | % | m3 | Nm3 | % | % | ppm | ppm | - | -
2023-02-01 | 1.7 | 14.12 | 15.82 | 830.359 | 19.052 | 7.18 | 538.9 | 979 | 725 | 54.9 | 57.5 | 7.05 | 449.1 | 965 | 560 | - | - | - | 2023-02-01 | 745 | 6.94 | 900 | 569.1 | 940 | 243 | 6.49 | 31 | 15.1 | 97 | 9890 | 6.54 | 13 | 11.1 | 87 | 12360 | 2023-02-01 | 7.06 | 7.9 | 64 | 9 | 5.5 | 14 | 6.56 | 8.1 | 64 | 9.2 | 600 | 0 | 0.2 | 2023-02-01 | 6.5 | 1.055 | 5870 | 3395 | 595 | 101.2792 | 6.46 | 0.9 | 6435 | 3905 | 700 | 108.758 | 2023-02-01 | 6.36 | 4.1375 | 55.505 | 6.31 | 5.53 | 53.71 | 612 | 850 | 0.72 | 139 | 2023-02-01 | 6.94 | 5.64 | 44.49 | 1104 | 1725 | 0.64 | 27.34 | 6.53 | 6 | 46.84 | 1300 | 1032 | 1.2597 | 17.56 | 2023-02-01 | - | - | - | - | - | 59 | - | - | - | 283 | 86 | 6.81 | 3.1
2023-02-02 | 1.7 | 14.49 | 16.19 | 927.103 | 17.463 | 7.09 | 449.2 | 783 | 550 | 48.2 | 75 | 7.03 | 478.9 | 1098 | 590 | - | 45000000 | 23000000 | 2023-02-02 | 530 | 7.09 | 835 | 508.9 | 1057 | 248 | 6.71 | 14 | 11.9 | 106 | 9430 | 6.59 | 15 | 12.9 | 69 | 14900 | 2023-02-02 | 7.22 | 6.2 | 59 | 8 | 8 | 12.3 | 6.98 | 7.9 | 91 | 9.6 | 520 | 100 | 0.2 | 2023-02-02 | 6.5 | 0.985 | 5845 | 4110 | 630 | 107.6915 | 6.52 | 0.775 | 6355 | 3935 | 700 | 110.139 | 2023-02-02 | 6.455 | 3.8875 | 59.69 | 6.42 | 5.42 | 58.54 | 708 | 900 | 0.78667 | 134 | 2023-02-02 | 6.91 | 5.94 | 49.46 | 1056 | 1725 | 0.61217 | 27.89 | 6.6 | 5.54 | 46.42 | 1308 | 1325 | 0.98717 | 17.68 | 2023-02-02 | 6.72 | 4.8 | 49.25 | 26.92 | 52.05 | 161 | - | - | - | 340 | 86 | 7 | 3.22
2023-02-03 | 1.8 | 13.82 | 15.62 | 831.8688 | 18.777 | 6.99 | 538.9 | 1076 | 650 | 55.4 | 68.5 | 7.21 | 689.2 | 1143 | 945 | - | 52000000 | 18000000 | 2023-02-03 | 465 | 7.01 | 660 | 419.2 | 979 | 287 | 6.71 | 21 | 12.2 | 64 | 15860 | 6.8 | 11 | 9.2 | 71 | 11900 | 2023-02-03 | 7.09 | 6.9 | 71 | 7.3 | 8.5 | 14 | 7.19 | 7.2 | 64 | 8.6 | 300 | 0 | 0.5 | 2023-02-03 | 6.505 | 0.94 | 5880 | 3215 | 625 | 106.2602 | 6.53 | 0.805 | 6305 | 4805 | 695 | 110.1538 | 2023-02-03 | 6.425 | 4.3075 | 44.835 | 6.39 | 5.7 | 54.83 | 708 | 575 | 1.2313 | 181 | 2023-02-03 | 6.94 | 5.86 | 40.68 | 1068 | 1068 | 1 | 27.85 | 6.74 | 5.56 | 41.59 | 1068 | 1150 | 0.9287 | 17.23 | 2023-02-03 | 6.68 | 4.85 | 49.64 | 21.15 | 50.35 | 162 | - | - | - | 225 | 86 | 6.94 | 3.18
2023-02-04 | 2.1 | 13.32 | 15.42 | 846.834 | 18.209 | 7.12 | 659 | 1037 | 800 | 67.2 | 55 | 7.11 | 628.9 | 1014 | 960 | - | 56000000 | 27000000 | 2023-02-04 | - | 7.02 | 1010 | 478.9 | 1057 | 294 | 6.91 | 14 | 12.9 | 87 | 12370 | 6.79 | 14 | 10.9 | 97 | 13360 | 2023-02-04 | 7.68 | 8 | 52 | 9.7 | 3.5 | 13.4 | 6.93 | 6.9 | 69 | 8.6 | 540 | 180 | 0.2 | 2023-02-04 | 6.505 | 0.955 | 5860 | 3655 | 660 | 112.6216 | 6.58 | 0.795 | 6080 | 4555 | 740 | 121.6833 | 2023-02-04 | 6.3225 | 3.84 | 47.5225 | 6.41 | 5.37 | 56.96 | 480 | 800 | 0.6 | 299 | 2023-02-04 | 6.97 | 4.72 | 44.28 | 1308 | 1308 | 1 | 27.12 | 6.67 | 5.71 | 48.08 | 1212 | 1450 | 0.83586 | 17.02 | 2023-02-04 | 6.77 | 5.65 | 48.11 | 21.8 | 49.2 | 165 | - | - | - | 283 | 56 | 6.92 | 3.07
2023-02-05 | 1.9 | 13.71 | 15.61 | 886.0257 | 17.618 | 7.4 | 389.5 | 916 | 475 | 75 | 65 | 7.48 | 569 | 1032 | 635 | - | 45000000 | 22000000 | 2023-02-05 | 590 | 7.2 | 1666 | 539 | 1001 | 283 | 7.28 | 20 | 11 | 57 | 10010 | 7.15 | 15 | 11 | 48 | 14890 | 2023-02-05 | 7.27 | 6.3 | 64 | 6.7 | 6 | 18.5 | 7.47 | 7 | 60 | 8.8 | 0 | 0 | 0.2 | 2023-02-05 | 6.845 | 0.745 | 6085 | 4400 | 790 | 129.871 | 6.815 | 0.655 | 6635 | 4810 | 710 | 107.0095 | 2023-02-05 | 6.5575 | 3.7925 | 58.0775 | 6.54 | 4.12 | 60.08 | 552 | 475 | 1.1621 | 166 | 2023-02-05 | 7.1 | 4.4 | 48.36 | 1008 | 1975 | 0.51038 | 27.24 | 6.56 | 5.49 | 54.55 | 1068 | 1275 | 0.83765 | 17.45 | 2023-02-05 | 6.8 | 4.75 | 51.72 | 22.68 | 47 | 169 | - | - | - | 340 | 86 | 6.71 | 2.91
2023-02-06 | 2.3 | 13.76 | 16.06 | 919.8694 | 17.459 | 7.11 | 539.6 | 943 | 660 | 53.8 | 52.5 | 7.37 | 509.5 | 960 | 540 | - | 55000000 | 31000000 | 2023-02-06 | 545 | 7.29 | 735 | 299.5 | 657 | 296 | 7.11 | 14 | 13.5 | 50 | 8960 | 7.16 | 35 | 12.5 | 74 | 14660 | 2023-02-06 | 7 | 6.4 | 55 | 8.3 | 8.5 | 11.8 | 7.22 | 6.3 | 52 | 9.6 | 420 | 80 | 0.5 | 2023-02-06 | 6.775 | 0.74 | 5780 | 3650 | 735 | 127.1626 | 6.685 | 0.77 | 6660 | 4775 | 745 | 111.8606 | 2023-02-06 | 6.5275 | 4.2475 | 52.5525 | 6.56 | 5.37 | 55.58 | 576 | 875 | 0.65829 | 196 | 2023-02-06 | 7.77 | 5.75 | 43.7 | 1704 | 2150 | 0.79256 | 27.9 | 6.5 | 5.53 | 48.6 | 1200 | 1750 | 0.68571 | 17.88 | 2023-02-06 | 6.81 | 4.74 | 48.09 | 21.08 | 51.71 | 171 | - | - | - | 340 | 170 | 6.66 | 2.8
2023-02-07 | 1.7 | 14.05 | 15.75 | 917.4579 | 17.167 | 6.99 | 569.1 | 1030 | 610 | 31.4 | 99.5 | 7 | 539.6 | 1003 | 695 | - | 61000000 | 19000000 | 2023-02-07 | 765 | 7 | 600 | 359.6 | 756 | 279 | 6.85 | 22 | 14.6 | 72 | 9350 | 7.09 | 12 | 9.6 | 73 | 13910 | 2023-02-07 | 6.94 | 7.7 | 55 | 10.7 | 5.5 | 13.4 | 7 | 6.4 | 60 | 9.2 | 280 | 0 | 0.2 | 2023-02-07 | 6.635 | 0.805 | 5720 | 3100 | 785 | 137.3093 | 6.705 | 0.845 | 6660 | 4505 | 760 | 113.9908 | 2023-02-07 | 6.4275 | 3.5275 | 57.1325 | 6.52 | 4.92 | 57.14 | 708 | 775 | 0.91355 | 184 | 2023-02-07 | 6.92 | 5.53 | 45.06 | 1140 | 2050 | 0.5561 | 26.5 | 6.64 | 4.99 | 49.17 | 1008 | 1475 | 0.68339 | 16.7 | 2023-02-07 | 6.86 | 4.51 | 49.71 | 22.49 | 54.82 | 167 | - | - | - | 283 | 86 | 7.02 | 2.94
2023-02-08 | 2.3 | 12.24 | 14.54 | 798.5939 | 18.207 | 7 | 479.1 | 977 | 610 | 47.6 | 53.5 | 7.01 | 599.1 | 1061 | 660 | - | 64000000 | 35000000 | 2023-02-08 | 590 | 6.96 | 835 | 419.1 | 1030 | 250 | 6.79 | 25 | 16.1 | 62 | 10180 | 6.68 | 19 | 13.1 | 57 | 14060 | 2023-02-08 | 7 | 8.1 | 43 | 9.7 | 7.5 | 9.5 | 6.81 | 7.4 | 55 | 8.6 | 600 | 240 | 0.2 | 2023-02-08 | 6.68 | 0.84 | 5475 | 3330 | 665 | 120.3837 | 6.78 | 0.965 | 6380 | 3920 | 735 | 115.2185 | 2023-02-08 | 6.5025 | 3.9625 | 55.3325 | 6.54 | 4.45 | 56.11 | 960 | 775 | 1.2387 | 181 | 2023-02-08 | 6.94 | 4.41 | 44.68 | 1332 | 1750 | 0.76114 | 26.9 | 6.65 | 6.33 | 45.89 | 1284 | 1525 | 0.84197 | 16.8 | 2023-02-08 | 6.79 | 4.37 | 49.67 | 22.62 | 52.11 | 168 | - | - | - | 340 | 170 | 6.94 | 3.02
2023-02-09 | 1.7 | 14.33 | 16.03 | 727.0171 | 22.049 | 7 | 568.9 | 1001 | 645 | 45.9 | 58.5 | 7.14 | 509.1 | 1073 | 690 | - | 52000000 | 25000000 | 2023-02-09 | 605 | 7 | 1050 | 539.1 | 1001 | 318 | 6.5 | 11 | 10.1 | 110 | 9940 | 6.71 | 23 | 14.1 | 57 | 14300 | 2023-02-09 | 7.17 | 8.7 | 48 | 9.7 | 4.5 | 7.3 | 7 | 7.4 | 43 | 8.6 | 0 | 0 | 0.2 | 2023-02-09 | 6.66 | 0.78 | 5740 | 3655 | 745 | 129.7165 | 6.645 | 0.81 | 6025 | 3865 | 745 | 124.1244 | 2023-02-09 | 6.4175 | 3.9275 | 54.0625 | 6.33 | 5 | 56.86 | 816 | 550 | 1.4836 | 188 | 2023-02-09 | 7 | 5.81 | 49.06 | 984 | 2025 | 0.48593 | 27.5 | 6.75 | 5.24 | 47.59 | 1188 | 1450 | 0.81931 | 17.3 | 2023-02-09 | 6.8 | 4.61 | 50.54 | 22.31 | 55.28 | 175 | - | - | - | 340 | 170 | 7.02 | 3.14
2023-02-10 | 2.1 | 13.25 | 15.35 | 695.2623 | 22.078 | 7.19 | 689.1 | 998 | 765 | 37.5 | 55 | 7.2 | 658.9 | 977 | 775 | - | 44000000 | 35000000 | 2023-02-10 | 870 | 7 | 865 | 688.9 | 1054 | 335 | 6.8 | 22 | 16.9 | 60 | 10170 | 6.85 | 24 | 15.9 | 57 | 16050 | 2023-02-10 | 7.04 | 7.4 | 52 | 9.3 | 2.5 | 6.7 | 7.07 | 7.9 | 38 | 8.6 | 320 | 100 | 0.5 | 2023-02-10 | 6.98 | 0.86 | 5880 | 3920 | 755 | 128.6943 | 6.79 | 0.905 | 6410 | 4380 | 780 | 121.8646 | 2023-02-10 | 6.4625 | 4.005 | 50.95 | 6.38 | 4.36 | 52.4 | 720 | 350 | 2.0571 | 200 | 2023-02-10 | 6.99 | 4.57 | 44.59 | 1200 | 1875 | 0.64 | 27.5 | 6.6 | 6.09 | 44.07 | 1308 | 1450 | 0.90207 | 17.8 | 2023-02-10 | 6.71 | 4.66 | 47.5 | 22.07 | 56.88 | 174 | - | - | - | 283 | 141 | 6.86 | 3.04
2023-02-11 | 1.7 | 14.4 | 16.1 | 703.7636 | 22.877 | 6.94 | 539 | 1030 | 585 | 62.7 | 64 | 7.14 | 599.1 | 965 | 695 | - | 23000000 | 11000000 | 2023-02-11 | 750 | 6.97 | 1520 | 719.1 | 1032 | 328 | 6.78 | 17 | 13.1 | 55 | 10020 | 6.87 | 19 | 16.1 | 86 | 16170 | 2023-02-11 | 6.89 | 8 | 50 | 9 | 6 | 10.6 | 7.01 | 7.7 | 72 | 9.6 | 350 | 120 | 0.2 | 2023-02-11 | 6.91 | 0.7 | 5870 | 3170 | 765 | 131.3176 | 6.81 | 0.735 | 6560 | 3080 | 770 | 117.3337 | 2023-02-11 | 6.4375 | 3.93 | 50.49 | 6.42 | 5.53 | 53.9 | 1056 | 500 | 2.112 | 179 | 2023-02-11 | 6.99 | 4.34 | 46.76 | 1464 | 1850 | 0.79135 | 27.8 | 6.6 | 4.68 | 46.12 | 1500 | 1152 | 1.3021 | 17.5 | 2023-02-11 | 6.77 | 4.26 | 47.87 | 22.34 | 55.66 | 173 | - | - | - | 453 | 113 | 6.81 | 3.09
2023-02-12 | 2.3 | 13.42 | 15.72 | 694.6531 | 22.63 | 6.96 | 538.9 | 972 | 635 | 57.1 | 58.5 | 7.07 | 569 | 1132 | 610 | - | 50000000 | 15000000 | 2023-02-12 | 620 | 6.91 | 1290 | 449 | 1078 | 332 | 6.81 | 11 | 9 | 45 | 11850 | 6.78 | 10 | 9 | 64 | 13930 | 2023-02-12 | 7.4 | 7.2 | 45 | 8.3 | 6 | 9.5 | 6.84 | 7.6 | 40 | 8.6 | 420 | 50 | 0.2 | 2023-02-12 | 6.805 | 0.715 | 6190 | 4080 | 830 | 134.4946 | 6.745 | 0.805 | 6760 | 4590 | 815 | 120.4256 | 2023-02-12 | 6.4725 | 3.47 | 61.8475 | 6.53 | 4.94 | 61.71 | 636 | 425 | 1.4965 | 142 | 2023-02-12 | 7.08 | 4.12 | 53.45 | 1668 | 2025 | 0.8237 | 27.9 | 6.8 | 4.43 | 53.42 | 1236 | 1600 | 0.7725 | 17.8 | 2023-02-12 | 6.91 | 4.1 | 55.1 | 21.6 | 57.18 | 176 | - | - | - | 453 | 86 | 6.69 | 2.98
2023-02-13 | 1.8 | 14.01 | 15.81 | 715.8705 | 22.085 | 7.15 | 569.3 | 856 | 615 | 59 | 36.4 | 7.39 | 628.9 | 965 | 710 | - | 39000000 | 22000000 | 2023-02-13 | 870 | 7.09 | 855 | 478.9 | 1020 | 337 | 6.96 | 12 | 10.9 | 48 | 9410 | 7.17 | 18 | 15.9 | 52 | 15580 | 2023-02-13 | 7.34 | 7.9 | 33 | 8.7 | 5.5 | 4.5 | 7.32 | 8.3 | 33 | 9.2 | 550 | 70 | 0.2 | 2023-02-13 | 6.92 | 0.75 | 5915 | 3825 | 840 | 142.6275 | 6.905 | 0.85 | 6440 | 4515 | 680 | 105.6716 | 2023-02-13 | 6.5425 | 3.8425 | 59.0075 | 6.55 | 5.28 | 59.3 | 420 | 650 | 0.64615 | 159 | 2023-02-13 | 7.08 | 4.23 | 50.22 | 1512 | 1800 | 0.84 | 28.3 | 6.82 | 4.79 | 49.07 | 1020 | 1350 | 0.75556 | 18.1 | 2023-02-13 | 6.9 | 4.57 | 51.82 | 22.53 | 55.69 | 149 | - | - | - | 368 | 141 | 6.9 | 3.03
2023-02-14 | 2 | 13.71 | 15.71 | 714.7732 | 21.979 | 7.09 | 539.4 | 909 | 610 | 57.7 | 70 | 7.2 | 659.3 | 836 | 755 | - | 30000000 | 1000000 | 2023-02-14 | 795 | 7.02 | 840 | 479.3 | 495 | 301 | 7.05 | 12 | 11.3 | 38 | 11580 | 7.01 | 21 | 18.3 | 43 | 15810 | 2023-02-14 | 7.6 | 7.3 | 38 | 9.3 | 5 | 10.6 | 7.26 | 7.9 | 38 | 8.2 | 0 | 0 | 0.2 | 2023-02-14 | 6.895 | 0.755 | 5860 | 4140 | 805 | 137.2152 | 6.88 | 0.84 | 6640 | 4905 | 725 | 108.9075 | 2023-02-14 | 6.5425 | 4.2175 | 56.03 | 6.59 | 5.92 | 54.7 | 456 | 725 | 0.62897 | 189 | 2023-02-14 | 7.06 | 4.84 | 45.48 | 1608 | 1625 | 0.98954 | 28.4 | 6.86 | 5.34 | 46.41 | 1236 | 1275 | 0.96941 | 18.2 | 2023-02-14 | 6.92 | 4.85 | 48.31 | 22.17 | 55.71 | 173 | - | - | - | 453 | 141 | 6.76 | 2.96
2023-02-15 | 1.7 | 13.51 | 15.21 | 715.2262 | 21.266 | 7.21 | 569.7 | 841 | 695 | 39.8 | 44.5 | 7.35 | 599.4 | 894 | 660 | - | 40000000 | 38000000 | 2023-02-15 | 805 | 7.08 | 2165 | 449.4 | 507 | 332 | 7.08 | 15 | 12.4 | 52 | 9910 | 7.11 | 16 | 13.4 | 48 | 14100 | 2023-02-15 | 7.29 | 7.2 | 31 | 9 | 7 | 7.8 | 7.39 | 6.9 | 33 | 8.8 | 140 | 0 | 0.2 | 2023-02-15 | 6.945 | 0.75 | 6195 | 4020 | 805 | 129.9184 | 6.88 | 0.83 | 6775 | 4740 | 745 | 109.8319 | 2023-02-15 | 6.58 | 4.3325 | 53.615 | 6.61 | 5.8 | 54.72 | 612 | 475 | 1.2884 | 180 | 2023-02-15 | 7.16 | 4.63 | 44.9 | 1320 | 1900 | 0.69474 | 28.4 | 6.8 | 6.09 | 47.98 | 1104 | 1250 | 0.8832 | 18.4 | 2023-02-15 | 6.96 | 4.97 | 46.65 | 22.75 | 53.05 | 171 | - | - | - | 453 | 113 | 6.79 | 3.08
2023-02-16 | 2.6 | 12.09 | 14.69 | 681.7971 | 21.546 | 6.91 | 629.2 | 756 | 655 | 59.9 | 54 | 7.13 | 599.7 | 1006 | 925 | - | 53000000 | 25000000 | 2023-02-16 | 970 | 7.1 | 545 | 389.7 | 754 | 324 | 7.12 | 9 | 8.7 | 40 | 9970 | 7.06 | 16 | 13.7 | 45 | 15290 | 2023-02-16 | 7.36 | 6 | 50 | 9.7 | 7 | 8.4 | 7.36 | 7.2 | 40 | 8.6 | 350 | 110 | 0.5 | 2023-02-16 | 6.915 | 0.69 | 5755 | 3985 | 615 | 107.8842 | 6.875 | 0.57 | 7070 | 4810 | 640 | 90.5419 | 2023-02-16 | 6.55 | 3.54 | 64.1625 | 6.63 | 5.22 | 55.86 | 492 | 575 | 0.85565 | 142 | 2023-02-16 | 7.11 | 4.77 | 49.79 | 1344 | 1725 | 0.77913 | 28.2 | 6.92 | 4.9 | 55.36 | 1092 | 1175 | 0.92936 | 18.2 | 2023-02-16 | 6.98 | 4.32 | 52.91 | 22.93 | 55.29 | 160 | - | - | - | 283 | 170 | 6.6 | 3.02
2023-02-17 | 2.1 | 14.06 | 16.16 | 694.1581 | 23.28 | 7.05 | 688.9 | 1109 | 755 | 54.3 | 75.5 | 7.12 | 659.2 | 846 | 720 | - | 35000000 | 29000000 | 2023-02-17 | 715 | 7.09 | 1045 | 569.2 | 802 | 396 | 6.96 | 12 | 10.2 | 62 | 9850 | 6.96 | 16 | 14.2 | 79 | 17290 | 2023-02-17 | 7.24 | 6 | 62 | 8.7 | 6.5 | 9.5 | 7.09 | 6.3 | 38 | 9.6 | 650 | 100 | 0.2 | 2023-02-17 | 6.47 | 0.805 | 6120 | 4275 | 735 | 121.298 | 6.59 | 0.68 | 7415 | 5425 | 535 | 72.1381 | 2023-02-17 | 6.6275 | 4.12 | 60.465 | 6.58 | 5.28 | 59.45 | 576 | 400 | 1.44 | 147 | 2023-02-17 | 7.08 | 4.37 | 49.93 | 1416 | 1825 | 0.77589 | 28.5 | 6.76 | 5.72 | 49.86 | 1188 | 1725 | 0.6887 | 18.5 | 2023-02-17 | 6.98 | 4.83 | 56.72 | 22.51 | 61.45 | 170 | - | - | - | 283 | 170 | 6.82 | 4.15
2023-02-18 | 1.5 | 14.72 | 16.22 | 651.5103 | 24.896 | 6.91 | 628.9 | 938 | 670 | 33 | 66 | - | - | - | - | - | 31000000 | 23000000 | 2023-02-18 | - | - | - | - | - | 271 | - | - | - | - | - | - | - | - | - | - | 2023-02-18 | 7.43 | 6.8 | 40 | 7 | 8.5 | 7.3 | - | - | - | - | 620 | 110 | 0.2 | 2023-02-18 | - | - | - | - | - | - | - | - | - | - | - | - | 2023-02-18 | - | - | - | - | - | - | - | - | - | 156 | 2023-02-18 | - | - | - | - | - | - | 28.5 | - | - | - | - | - | - | 18.5 | 2023-02-18 | - | - | - | - | - | 174 | - | - | - | - | - | - | -
2023-02-19 | 2 | 14.11 | 16.11 | 788.8938 | 20.421 | 7.2 | 599.7 | 969 | 660 | 53.8 | 61 | 7.12 | 718.9 | 1030 | 870 | - | 46000000 | 34000000 | 2023-02-19 | 430 | 7.09 | 330 | 298.9 | 614 | 235 | 6.83 | 13 | 10.9 | 57 | 10340 | 6.96 | 16 | 11.9 | 48 | 13580 | 2023-02-19 | 7.3 | 6.5 | 40 | 8.3 | 7.5 | 9 | 7.08 | 6.4 | 52 | 8.6 | 550 | 0 | 0.5 | 2023-02-19 | 6.895 | 0.885 | 6645 | 4615 | 825 | 124.0929 | 6.935 | 0.7 | 7165 | 5140 | 655 | 91.5247 | 2023-02-19 | 6.505 | 3.8275 | 59.3025 | 6.38 | 4.85 | 57.14 | 624 | 425 | 1.4682 | 113 | 2023-02-19 | 7.14 | 4.74 | 50.58 | 1272 | 1800 | 0.70667 | 28.5 | 6.75 | 5.31 | 53.71 | 1116 | 1175 | 0.94979 | 18.5 | 2023-02-19 | 6.91 | 4.78 | 52.47 | 22.09 | 65.06 | 168 | - | - | - | 340 | 170 | 6.91 | 3.96
2023-02-20 | 1.6 | 13.84 | 15.44 | 644.1385 | 23.97 | 6.96 | 719 | 1001 | 845 | 35.3 | 57 | 7.03 | 629.7 | 1064 | 855 | - | 37000000 | 40000000 | 2023-02-20 | 855 | 7.06 | 855 | 449.7 | 979 | 151 | 7.08 | 24 | 15.7 | 48 | 10360 | 6.99 | 16 | 12.7 | 50 | 17940 | 2023-02-20 | 7.41 | 7.3 | 52 | 8.7 | 8 | 11.8 | 7.12 | 6.1 | 38 | 8.6 | 450 | 0 | 0.5 | 2023-02-20 | 6.82 | 0.94 | 6625 | 4550 | 790 | 119.1681 | 6.925 | 0.745 | 7675 | 5190 | 760 | 98.9589 | 2023-02-20 | 6.515 | 3.8675 | 68.0625 | 6.39 | 7.01 | 52.07 | 516 | 550 | 0.93818 | 159 | 2023-02-20 | 7.14 | 4.58 | 54.73 | 1452 | 1950 | 0.74462 | 28.7 | 6.81 | 5.33 | 57.08 | 1248 | 1175 | 1.0621 | 18.9 | 2023-02-20 | 6.92 | 4.46 | 55.44 | 21.65 | 55.29 | 160 | - | - | - | 283 | 170 | 7.02 | 4.04
2023-02-21 | 2.1 | 12.27 | 14.37 | 758.6717 | 18.941 | 7.05 | 539.2 | 979 | 655 | 31.4 | 79 | 7.1 | 749 | 1083 | 790 | - | 39000000 | 5000000 | 2023-02-21 | 840 | 6.96 | 1010 | 569 | 982 | 300 | 6.86 | 23 | 17 | 57 | 11000 | 6.96 | 19 | 15 | 62 | 15470 | 2023-02-21 | 7 | 7.8 | 52 | 8.3 | 4 | 11.8 | 7.05 | 7.3 | 48 | 9.2 | 560 | 160 | 0.2 | 2023-02-21 | 6.875 | 0.98 | 6435 | 3690 | 735 | 114.1962 | 6.82 | 0.78 | 7395 | 4345 | 755 | 102.3433 | 2023-02-21 | 6.5375 | 4.15 | 52.95 | 6.4 | 5.3 | 59.6 | 804 | 525 | 1.5314 | 241 | 2023-02-21 | 7.13 | 4.57 | 50.04 | 1476 | 1825 | 0.80877 | 29 | 6.84 | 5.71 | 48.95 | 1164 | 1100 | 1.0582 | 19 | 2023-02-21 | 6.9 | 4.83 | 50.47 | 23.21 | 56.56 | 176 | - | - | - | 340 | 170 | 6.84 | 3.92
2023-02-22 | 2.3 | 5.09 | 7.39 | 1221.8915 | 6.048 | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-02-22 | - | - | - | - | - | 288 | - | - | - | - | - | - | - |  | - | - | 2023-02-22 | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-02-22 | - | - | - | - | - | - | - | - | - | - | - | - | 2023-02-22 | - | - | - | - | - | - | - | - | - | 203 | 2023-02-22 | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 2023-02-22 | - | - | - | - | - | 167 | - | - | - | - | - | - | -
2023-02-23 | 2.2 | 10.91 | 13.11 | 579.0636 | 22.64 | 7.11 | 748.9 | 982 | 780 | 23.5 | 66 | 7.31 | 719.1 | 1105 | 850 | - | 50000000 | 22000000 | 2023-02-23 | 895 | 6.96 | 1690 | 659.1 | 969 | 264 | 6.81 | 18 | 13.1 | 57 | 12040 | 6.96 | 20 | 15.1 | 67 | 15930 | 2023-02-23 | 7.21 | 9 | 57 | 11.3 | 3.5 | 6.7 | 7.05 | 8.1 | 48 | 11.6 | 520 | 200 | 0.5 | 2023-02-23 | 6.805 | 0.975 | 6215 | 4040 | 665 | 107.4029 | 6.7 | 0.795 | 7480 | 5010 | 865 | 115.8049 | 2023-02-23 | 6.5375 | 4.2525 | 51.945 | 6.62 | 6.26 | 51.18 | 960 | 500 | 1.92 | 126 | 2023-02-23 | 7.04 | 4.47 | 48.17 | 1692 | 1775 | 0.95324 | 29 | 6.8 | 6.15 | 48.47 | 1032 | 1050 | 0.98286 | 19 | 2023-02-23 | 6.96 | 4.52 | 50.91 | 23.03 | 55.96 | 173 | - | - | - | 226 | 113 | 6.83 | 3.67
2023-02-24 | 1.5 | 13.86 | 15.36 | 652.5064 | 23.54 | 7.24 | 659.3 | 948 | 805 | 35.3 | 57.5 | 7.04 | 718.9 | 1020 | 790 | - | 30000000 | 15000000 | 2023-02-24 | - | 6.94 | 515 | 478.9 | 938 | 331 | 6.83 | 20 | 14.9 | 64 | 9030 | 6.88 | 19 | 12.9 | 110 | 14880 | 2023-02-24 | 7.28 | 8.3 | 33 | 10.3 | 6 | 10.1 | 7 | 7.2 | 50 | 11.4 | 0 | 0 | 0.5 | 2023-02-24 | 6.735 | 0.71 | 6740 | - | 780 | 116.2357 | 6.765 | 0.615 | 7530 | - | 860 | 114.1505 | 2023-02-24 | 6.5275 | 3.7875 | 56.0875 | 6.44 | 5.45 | 57.69 | 816 | 500 | 1.632 | 149 | 2023-02-24 | 7.01 | 4.49 | 48.2 | 1584 | 1775 | 0.89239 | 29 | 6.76 | 4.92 | 52.12 | 1128 | 1175 | 0.96 | 19 | 2023-02-24 | - | - | - | - | - | 88 | - | - | - | 340 | 141 | 7.01 | 3.51
2023-02-25 | 2 | 13.5 | 15.5 | 800.4958 | 19.363 | 6.8 | 659.2 | 1003 | 875 | 64.4 | 64 | 7.09 | 629.3 | 977 | 705 | - | 42000000 | 22000000 | 2023-02-25 | 770 | 6.99 | 690 | 509.3 | 558 | 301 | 6.91 | 14 | 11.3 | 40 | 10510 | 6.93 | 16 | 13.3 | 48 | 15260 | 2023-02-25 | 7.43 | 8.2 | 48 | 9.3 | 7 | 14.6 | 7.02 | 7.9 | 26 | 9.4 | 640 | 120 | 0.5 | 2023-02-25 | 6.72 | 0.835 | 6425 | 4280 | 745 | 115.796 | 6.76 | 0.775 | 7415 | 4990 | 860 | 115.885 | 2023-02-25 | 6.5375 | 3.965 | 58.2125 | 6.38 | 4.82 | 51.93 | 708 | 525 | 1.3486 | 242 | 2023-02-25 | 7.07 | 4.57 | 48.28 | 1452 | 1600 | 0.9075 | 29 | 6.78 | 5.58 | 49.78 | 1260 | 1325 | 0.95094 | 19 | 2023-02-25 | 6.91 | 4.43 | 51.47 | 21.26 | 59.61 | 172 | - | - | - | 453 | 85 | 6.99 | 4.05
2023-02-26 | 2 | 13.39 | 15.39 | 715.1487 | 21.52 | 6.69 | 689.5 | 952 | 775 | 21.8 | 71.5 | 7.15 | 629.2 | 902 | 805 | - | 50000000 | 31000000 | 2023-02-26 | 935 | 6.98 | 840 | 509.2 | 1057 | 282 | 6.96 | 19 | 16.2 | 72 | 11010 | 6.98 | 30 | 17.2 | 118 | 17910 | 2023-02-26 | 7.13 | 8.5 | 28 | 9.3 | 7 | 11.8 | 7.33 | 7.1 | 38 | 8 | 520 | 200 | 0.2 | 2023-02-26 | 6.695 | 0.92 | 6455 | 4150 | 775 | 119.8164 | 6.9 | 0.665 | 7795 | 5365 | 840 | 107.8556 | 2023-02-26 | 6.5125 | 3.835 | 56.6925 | 6.42 | 4.71 | 46.29 | 828 | 525 | 1.5771 | 188 | 2023-02-26 | 7.04 | 4.5 | 49.09 | 1692 | 1825 | 0.92712 | 29 | 6.79 | 4.96 | 51.28 | 1452 | 1325 | 1.0958 | 19 | 2023-02-26 | 6.5125 | 3.835 | 56.6925 | 23.74 | 51.34 | 166 | - | - | - | 453 | 141 | 7.07 | 3.87
2023-02-27 | 2.2 | 12.59 | 14.79 | 787.9595 | 18.77 | 7.02 | 629.6 | 909 | 670 | 49.3 | 50.5 | 7.05 | 659.5 | 1076 | 720 | - | 21000000 | 1000000 | 2023-02-27 | 455 | 6.95 | 155 | 239.5 | 674 | 293 | 6.78 | 29 | 18.5 | 69 | 8820 | 6.81 | 28 | 19.5 | 55 | 17450 | 2023-02-27 | 7.18 | 7.9 | 40 | 8.7 | 7 | 10.1 | 6.96 | 8.1 | 38 | 9 | 450 | 0 | 0.2 | 2023-02-27 | 6.735 | 0.905 | 6370 | 4080 | 825 | 129.5207 | 6.685 | 0.8 | 7675 | 5230 | 940 | 122.5782 | 2023-02-27 | 6.3825 | 4.0925 | 59.68 | 6.33 | 5.5 | 60.67 | 732 | 450 | 1.6267 | 170 | 2023-02-27 | 6.88 | 4.38 | 49.84 | 1524 | 2075 | 0.73446 | 29 | 6.56 | 4.89 | 52.86 | 1368 | 1550 | 0.88258 | 19 | 2023-02-27 | 6.3825 | 4.0925 | 59.68 | 21.9 | 58 | 176 | - | - | - | 538 | 141 | 6.97 | 3.69
2023-02-28 | 2.3 | 11.84 | 14.14 | 660.439 | 21.41 | 6.77 | - | 950 | 670 | 64.4 | 50.5 | 7.11 | 689.6 | 1136 | 735 | - | 47000000 | 36000000 | 2023-02-28 | 670 | 6.98 | 1165 | 509.6 | 1139 | 292 | 6.77 | 10 | 9.6 | 52 | 9740 | 6.79 | 18 | 15.6 | 50 | 16430 | 2023-02-28 | 7.43 | - | 31 | 8.3 | 6.5 | 11.8 | 7.13 | 8.2 | 40 | 9.2 | 620 | 240 | 0.5 | 2023-02-28 | 6.71 | 0.73 | 6305 | 3965 | 740 | 117.1784 | 6.69 | 0.575 | 7480 | 4905 | 850 | 113.7209 | 2023-02-28 | 6.4225 | 3.9325 | 52.3975 | 6.36 | 5.24 | 54.46 | 550 | 693.6 | 0.79296 | 193 | 2023-02-28 | 6.91 | 4.46 | 44.89 | 1416 | 1950 | 0.72615 | 29 | 6.59 | 5.71 | 45.65 | 1236 | 1425 | 0.86737 | 19 | 2023-02-28 | 6.79 | 4.64 | 48.72 | 21.31 | 54.8867 | 174 | - | - | - | 453 | 113 | 7.08 | 4.01
AVG | 1.9714 | 13.1575 | 15.1289 | 770.0483 | 20.1879 | 7.0419 | 591.1154 | 957.1852 | 683.1481 | 48.8741 | 61.7 | 7.1538 | 618.8115 | 1013.9615 | 740.1923 |  | 43730769.2308 | 23269230.7692 | AVG | 711.6667 | 7.0262 | 948.6923 | 483.8115 | 889.6154 | 292.5357 | 6.8746 | 17.3846 | 12.9654 | 62.3462 | 10446.1538 | 6.9069 | 18.4231 | 13.6192 | 65.9615 | 15131.1538 | AVG | 7.2367 | 7.4423 | 47.8889 | 8.9111 | 6.2222 | 10.6222 | 7.0862 | 7.3385 | 48.7692 | 9.1154 | 406.2963 | 80.7407 | 0.31111 | AVG | 6.7475 | 0.83654 | 6086.7308 | 3891.8 | 740.7692 | 121.8905 | 6.7452 | 0.76865 | 6892.8846 | 4627.8 | 754.0385 | 109.7106 | AVG | 6.488 | 3.9537 | 56.0234 | 6.4627 | 5.2827 | 55.88 | 677.9231 | 591.1 | 1.2367 | 176.6429 | AVG | 7.0538 | 4.7958 | 47.6427 | 1376.7692 | 1806.7692 | 0.77283 | 28.1459 | 6.7108 | 5.4227 | 49.2662 | 1204.7692 | 1334.9615 | 0.91892 | 18.1119 | AVG | 6.8185 | 4.6011 | 51.2276 | 22.4225 | 55.0057 | 162.0357 |  |  |  | 354.9615 | 127.5 | 6.8835 | 3.3635
Remarks: | [18 empty] | Remarks: | [30 empty] | Remarks: | [12 empty] | Remarks: | [10 empty] | Remarks: | [14 empty] | Remarks:
*BDL - Below Detectable Limit, ([-] - analysis not conducted) | [18 empty] | *BDL - Below Detectable Limit | [16 empty] | *BDL - Below Detectable Limit | [13 empty] | *BDL - Below Detectable Limit | [12 empty] | *BDL - Below Detectable Limit | [10 empty] | *BDL - Below Detectable Limit | [14 empty] | *BDL - Below Detectable Limit
VA TECH WABAG | [14 empty] | PID | KVWSMB |  |  | VA TECH WABAG | [7 empty] | PID |  |  |  |  | KVWSMB |  |  |  | VA TECH WABAG | [9 empty] | PID | KVWSMB |  |  | VA TECH WABAG |  |  |  |  | PID |  |  |  | KVWSMB |  |  |  | VA TECH WABAG |  |  |  |  | PID |  |  | KVWSMB |  |  | VA TECH WABAG |  |  |  |  | PID |  |  |  |  | KVWSMB |  |  |  |  | VA TECH WABAG | [9 empty] | PID |  | KVWSMB
CHEMIST |  |  |  |  | PLANT INCHARGE | [6 empty] | PLANT INCHARGE | [6 empty] | CHEMIST |  | PLANT INCHARGE | [14 empty] | CHEMIST | [7 empty] | PLANT INCHARGE | [5 empty] | CHEMIST |  | PLANT INCHARGE | [10 empty] | CHEMIST |  | PLANT INCHARGE | [8 empty] | CHEMIST |  | PLANT INCHARGE | [12 empty] | CHEMIST |  |  | PLANT INCHARGE
Formulas:
Date = [Date]
Aeration Tank = [Date]
Digester Sludge Feeding Details = [Aeration Tank]
Digester Performance Details = [Digester Sludge Feeding Details]
Digester Outlet = [Digester Performance Details]