## Lab Report - March 2023
s | [18 empty] | s | [16 empty] | s | [13 empty] | s | [12 empty] | s | [10 empty] | s | [14 empty] | s
KATHMANDU, NEPAL | [18 empty] | KATHMANDU, NEPAL | [16 empty] | KATHMANDU, NEPAL | [13 empty] | KATHMANDU, NEPAL | [12 empty] | KATHMANDU, NEPAL | [10 empty] | KATHMANDU, NEPAL | [14 empty] | KATHMANDU, NEPAL
Project No: | 10M170 | [13 empty] | Month: | 2023-03-01 |  |  | Project No: | 10M170 | [10 empty] | Month: |  |  | 2023-03-01 |  | Project No: | 10M170 | [8 empty] | Month: | 2023-03-01 |  |  | Project No: |  | 10M170 | [6 empty] | Month: | 2023-03-01 |  |  | Project No: | 10M170 | [6 empty] | Month: | 2023-03-01 |  | Project No: |  | 10M170 | [7 empty] | Month: | 2023-03-01 |  |  |  | Project No: | 10M170 | [9 empty] | Month: | 2023-03-01
Date | Power Generation and Consumption |  |  |  | Inlet | [13 empty] | Date | Grit Classifier Outlet | Primary Clarifier |  |  |  |  | Secondary Clarifier |  |  |  |  | Secondary Sedimentation tank Outlet |  |  |  |  | Date | CHLORINE CONTACT TANK (Composite) | [5 empty] | CHLORINE CONTACT TANK | [6 empty] | Aeration Tank | [12 empty] | Digester Sludge Feeding Details | [10 empty] | Digester Performance Details | [14 empty] | Digester Outlet |  |  |  | Centrifuge |  |  | Bio Gas |  |  | Scrubber |  | Odour Control Unit
| Power Generation from Gas Engine | Daily Power Consumption from NEA (MW) | Total Power Consumption from NEA & GE (MW) | Total Power (KWh)/Flow (ML) | Raw Sewage Flow | Raw Sewage (Composite) | [5 empty] | Raw Sewage | [37 empty] | DATE | Existing Aeration Tank | [5 empty] | New Aeration Tank | [5 empty] | DATE | Primary sedimentation tank Underflow |  |  | Thickener Sludge Parameters | [6 empty] | DATE | Digester - A | [6 empty] | Digester - B | [6 empty] | DATE | Centrifuge Feed |  |  | Centrifuge Cake |  | Centrifuge Feed Totalizer | Gas Generation | Methane | Carbon Dioxide | Inlet | Outlet
[6 empty] | pH | BOD5 | COD | TSS | NH3-N | O & G | pH | BOD5 | COD | TSS | PO4 | Total Coliform | Fecal coliform |  | TSS | PH | TSS | BOD5 | COD | PST Sludge Totalizer | PH | TSS | BOD5 | COD | Existing RAS | PH | TSS | BOD5 | COD | New RAS |  | pH | BOD5 | COD | TSS | O & G | Ammonical Nitrogen | pH | BOD5 | COD | TSS | Total Coliform | Fecal coliform | FRC |  | PH | DO | MLSS | MLVSS | SV30 | SVI | PH | DO | MLSS | MLVSS | SV30 | SVI |  | pH | TS | VS | pH | TS | VS | VFA | Alkalinity | VFA/ Alkalinity Ratio | Digester Feed Totalizer |  | pH | TS | VS | VFA - mg/l | Alkalinity | VFA/ Alkalinity Ratio | Temp | pH | TS | VS | VFA - mg/l | Alkalinity | VFA/ Alkalinity Ratio | Temp |  | PH | TS | VS | TS | VS |  |  | CH4 | CO2 | H2S | H2S | Inlet pH | Outlet pH
Control Limits |  |  |  |  | 32.4 | 6.0 - 9.0 | 300 | 800 | 400 | 79 | 120 | 6.0 - 9.0 | 300 | 800 | 400 | 12 | 107-109 | 106-107 | Control Limits | - | [15 empty] | Control Limits | 6.5-8.0 | < 10 | < 250 | < 10 | < 10 | < 50 | 6.5-8.0 | < 10 | < 250 | < 10 | < 500 | < 100 | Max 1 | Control Limits | - | > 0.5 | - | - | - | - | - | > 0.5 | - | - | - | - | Control Limits | [10 empty] | Control Limits | [14 empty] | Control Limits
Units | MW | <482.02 KWh / ML of Treated Water |  |  | MLD | - | mg/L | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Units | mg/L | - | mg/L | mg/L | mg/L | m3 | - | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | mg/L | Units | - | mg/L | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | MPN /100ml | MPN /100ml | mg/L | Units | - | mg/L | mg/L | mg/L | ml/L | - | - | mg/L | mg/L | mg/L | ml/L | - | Units | - | % | % | - | % | % | mg/l | mg/l | - | m3 | Units | - | % | % | mg/l | mg/l | - | 0C | - | % | % | mg/l | mg/l | - | 0C | Units | - | % | % | % | % | m3 | Nm3 | % | % | ppm | ppm | - | -
2023-03-01 | 2.1 | 12.24 | 14.34 | 687.9348 | 20.845 | 6.89 | 689.2 | 979 | 790 | 32.5 | 63.5 | 7.05 | 659.3 | 977 | 700 | - | 300000000 | 24000000 | 2023-03-01 | 900 | 6.79 | 1860 | 629.3 | 742 | 284 | 6.8 | 16 | 12.3 | 40 | 11050 | 6.86 | 17 | 15.3 | 48 | 14320 | 2023-03-01 | 7.11 | 8.2 | 69 | 11.7 | 3 | 15.7 | 7.1 | 8.3 | 40 | 8.3 | 660 | 320 | 0.5 | 2023-03-01 | 6.72 | 0.8 | 6260 | 4025 | 875 | 139.7983 | 6.73 | 0.665 | 7585 | 5060 | 935 | 123.2752 | 2023-03-01 | 6.46 | 4.1225 | 62.065 | 6.39 | 4.87 | 59.83 | 552 | 400 | 1.38 | 157 | 2023-03-01 | 6.93 | 4.48 | 49.71 | 1548 | 2025 | 0.76444 | 29 | 6.58 | 5.47 | 51.71 | 1116 | 1425 | 0.78316 | 19 | 2023-03-01 | 6.83 | 4.3965 | 53.3019 | 21.81 | 53.65 | 168 | - | - | - | 453 | 141 | 6.32 | 3.27
2023-03-02 | 2 | 12.38 | 14.38 | 714.996 | 20.112 | 6.72 | 719.6 | 894 | 785 | 32.5 | 79 | 7.04 | 629.2 | 1020 | 760 | - | 53000000 | 31000000 | 2023-03-02 | 950 | 7 | 1515 | 509.2 | 938 | 276 | 6.82 | 21 | 18.2 | 64 | 12960 | 6.8 | 26 | 20.2 | 110 | 14730 | 2023-03-02 | 6.97 | 8.2 | 64 | 9.3 | 9 | 17.9 | 6.97 | 8.2 | 72 | 12 | 800 | 180 | 0.2 | 2023-03-02 | 6.805 | 0.71 | 6595 | - | 800 | 121.5628 | 6.785 | 0.74 | 7705 | - | 925 | 120.0566 | 2023-03-02 | - | - | - | - | - | - | - | - | - | 179 | 2023-03-02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-03-02 | - | ` | - | - | - | 161 | - | - | - | 340 | 170 | 7.04 | 3.81
2023-03-03 | 1.8 | 13.18 | 14.98 | 719.95 | 20.807 | 7.11 | 629.7 | 1146 | 725 | 41.4 | 95.5 | 7.03 | 689.6 | 996 | 755 | - | 41000000 | 27000000 | 2023-03-03 | 1075 | 6.9 | 2350 | 569.6 | 749 | 301 | 7.09 | 16 | 13.6 | 89 | 8970 | 7.07 | 16 | 14.6 | 118 | 15790 | 2023-03-03 | 6.98 | 6.8 | 79 | 9.7 | 7 | 9 | 7.39 | 7.9 | 48 | 9.2 | 510 | 120 | 0.2 | 2023-03-03 | 6.71 | 0.755 | 6080 | 3960 | 850 | 139.8547 | 6.745 | 0.73 | 6815 | 3985 | 925 | 135.7526 | 2023-03-03 | 6.5175 | 3.57 | 66.4725 | - | - | - | - | - | - | 49 | 2023-03-03 | 6.85 | 4.57 | 55.32 | 1020 | 1875 | 0.544 | 29 | 6.64 | 5.28 | 54.35 | 828 | 1300 | 0.63692 | 19 | 2023-03-03 | 6.88 | 3.8546 | 53.6585 | 23.98 | 52.06 | 78 | - | - | - | 538 | 170 | 6.38 | 2.77
2023-03-04 | 2 | 13.81 | 15.81 | 649.7349 | 24.333 | 7.08 | 599.5 | 819 | 650 | 35.8 | 73.5 | 7.05 | 659.7 | 1020 | 755 | - | 34000000 | 1000000 | 2023-03-04 | 740 | 7.01 | 915 | 539.7 | 1161 | 300 | 6.82 | 16 | 14.7 | 86 | 9460 | 6.78 | 23 | 15.7 | 69 | 13640 | 2023-03-04 | 6.98 | 9.6 | 48 | 10.3 | 7.5 | 9 | 6.94 | 6.5 | 48 | 9.6 | 0 | 0 | 0.5 | 2023-03-04 | 6.67 | 0.795 | 6275 | 3440 | 825 | 131.3771 | 6.71 | 0.61 | 7455 | 4190 | 930 | 124.7696 | 2023-03-04 | 6.51 | 4.1675 | 63.0875 | 6.41 | 4.918 | 61.6457 | 516 | 475 | 1.0863 | 117 | 2023-03-04 | 6.83 | 3.93 | 53.14 | 1128 | 1875 | 0.6016 | 29 | 6.7 | 4.77 | 55.99 | 1164 | 1300 | 0.89538 | 19 | 2023-03-04 | 6.84 | 4.0869 | 53.9394 | 21.4137 | 53.8023 | 162 | - | - | - | 453 | 113 | 6.59 | 2.8
2023-03-05 | 1.8 | 9.9 | 11.7 | 634.8345 | 18.43 | 7 | - | 909 | 670 | 21.8 | 85 | 7.02 | 629.5 | 1020 | 780 | - | 38000000 | 20000000 | 2023-03-05 | 780 | 7 | 820 | 539.5 | 723 | 284 | 6.79 | 16 | 13.5 | 118 | 9260 | 6.8 | 18 | 16.5 | 169 | 16590 | 2023-03-05 | 7.22 |  | 40 | 8 | 5 | 5.2 | 6.94 | 8.9 | 40 | 9.2 | 670 | 240 | 0.2 | 2023-03-05 | 6.68 | 0.77 | 5715 | 4725 | 855 | 150.5853 | 6.635 | 0.745 | 7360 | 5260 | 955 | 129.9124 | 2023-03-05 | 6.525 | 3.64 | 58.005 | 6.44 | 4.57 | 56.4 | 456 | 400 | 1.14 | 156 | 2023-03-05 | 6.88 | 4.14 | 50.09 | 1092 | 1700 | 0.64235 | 29 | 6.74 | 5.73 | 51.08 | 1140 | 1475 | 0.77288 | 19 | 2023-03-05 | 6.79 | 4.2847 | 49.6575 | 22.07 | 56.34 | 157 | - | - | - | 283 | 170 | 6.81 | 3.27
2023-03-06 | 2.4 | 11.22 | 13.62 | 942.1042 | 14.457 | 7.02 | 599.9 | 909 | 645 | 31.9 | 50.5 | - | - | - | - | - | 24000000 | 1000000 | 2023-03-06 | - | - | - | - | - | 283 | - | - | - | - | - | - | - | - | - | - | 2023-03-06 | 7.42 | 10 | 48 | 11 | 4 | 12.9 | - | - | - | - | 450 | 120 | 0.2 | 2023-03-06 | - | - | - | - | - | - | - | - | - | - | - | - | 2023-03-06 | - | - | - | - | - | - | - | - | - | 141 | 2023-03-06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-03-06 | - | - | - | - | - | 169 | - | - | - | - | - | - | -
2023-03-07 | 1.8 | 12.12 | 13.92 | 776.2659 | 17.932 | 7 | 599.6 | 969 | 785 | 28 | 41.5 | 7 | 449.9 | 1136 | 830 | - | 44000000 | 3000000 | 2023-03-07 | 695 | 6.98 | 1660 | 359.9 | 1076 | 357 | 7.05 | 19 | 13.9 | 54 | 8450 | 7.03 | 13 | 11.9 | 50 | 12320 | 2023-03-07 | 7.27 | 8.6 | 52 | 9.3 | 4.5 | 13.4 | 7.39 | 9.7 | 33 | 10.8 | 0 | 0 | 0.5 | 2023-03-07 | 6.66 | 0.87 | 5745 | 3465 | 770 | 134.0852 | 6.55 | 0.695 | 7210 | 4800 | 945 | 131.0673 | 2023-03-07 | 6.44 | 3.6825 | 57.0975 | 6.36 | 5.16 | 58.75 | 888 | 500 | 1.776 | 143 | 2023-03-07 | 7 | 4.23 | 50.27 | 1008 | 1600 | 0.63 | 29 | 6.78 | 5.65 | 56.77 | 1128 | 1400 | 0.80571 | 19 | 2023-03-07 | 6.88 | 4.0764 | 51.9868 | 21.97 | 57.5 | 173 | - | - | - | 453 | 141 | 7.02 | 3.21
2023-03-08 | 1.8 | 10.47 | 12.27 | 594.5055 | 20.639 | 7.12 | 539.4 | 977 | 700 | 54.3 | 65.5 | 7.08 | 569.6 | 977 | 705 | - | 57000000 | 29000000 | 2023-03-08 | 680 | 7 | 1420 | 779.6 | 614 | 383 | 6.9 | 15 | 13.4 | 48 | 9756 | 6.92 | 18 | 14 | 57 | 11660 | 2023-03-08 | 7.19 | 7.7 | 44 | 8 | 6 | 11.8 | 7.14 | 7.9 | 40 | 8.4 | 0 | 0 | 0.2 | 2023-03-08 | 6.66 | 0.8 | 5965 | 3215 | 785 | 131.5975 | 6.595 | 0.565 | 7400 | 4595 | 850 | 114.8112 | 2023-03-08 | 6.4725 | 3.4675 | 59.3475 | 6.4 | 5.18 | 61.27 | 720 | 525 | 1.3714 | 126 | 2023-03-08 | 7.01 | 4.21 | 51.25 | 1248 | 1825 | 0.68384 | 29 | 6.72 | 5.59 | 49.63 | 1020 | 1400 | 0.72857 | 19 | 2023-03-08 | 6.88 | 4.2501 | 51.9305 | 21.46 | 58.31 | 170 | - | - | - | 538 | 170 | 6.83 | 3.44
2023-03-09 | 1.6 | 9.51 | 11.11 | 609.4016 | 18.231 | 6.9 | 389.6 | 1061 | 570 | 42.6 | 49.5 | 7.01 | 569.4 | 1006 | 720 | - | 47000000 | 33000000 | 2023-03-09 | 570 | 7.03 | 1625 | 629.4 | 856 | 391 | 6.93 | 18 | 12.6 | 45 | 8240 | 6.93 | 26 | 13.8 | 64 | 15130 | 2023-03-09 | 7.09 | 5.6 | 52 | 9.7 | 8 | 9.5 | 7.15 | 8 | 50 | 8.8 | 520 | 270 | 0.5 | 2023-03-09 | 6.675 | 0.855 | 5240 | 3445 | 695 | 132.3967 | 6.605 | 0.56 | 7635 | 4635 | 895 | 117.2668 | 2023-03-09 | 6.5 | 3.4875 | 57.8575 | 6.36 | 5.66 | 59.43 | 624 | 675 | 0.92444 | 105 | 2023-03-09 | 6.97 | 4.48 | 50.33 | 1272 | 1775 | 0.71662 | 29 | 6.69 | 5.36 | 50.66 | 1092 | 1275 | 0.85647 | 19 | 2023-03-09 | 6.88 | 4.1405 | 48.4163 | 21.71 | 54.99 | 170 | - | - | - | 340 | 170 | 7 | 3.29
2023-03-10 | 1.8 | 15.17 | 16.97 | 794.6245 | 21.356 | 6.98 | 718.9 | 967 | 855 | 47 | 65 | 7 | 629.6 | 1030 | 880 | - | 53000000 | 24000000 | 2023-03-10 | 795 | 6.94 | 1740 | 629.6 | 960 | 407 | 6.81 | 19 | 14.6 | 64 | 7410 | 6.72 | 16 | 7.6 | 74 | 15820 | 2023-03-10 | 7.26 | 8.5 | 74 | 9 | 4.5 | 10.1 | 7.01 | 7.4 | 50 | 9 | 620 | 130 | 0.5 | 2023-03-10 | 6.86 | 0.83 | 5045 | 3395 | 715 | 142.2063 | 6.86 | 0.53 | 7930 | 4945 | 905 | 114.1324 | 2023-03-10 | 6.4375 | 3.735 | 67.305 | 6.38 | 5.6 | 61.21 | 576 | 525 | 1.0971 | 205 | 2023-03-10 | 7 | 4.47 | 54.05 | 1236 | 1825 | 0.67726 | 29 | 6.67 | 5.71 | 58.54 | 1104 | 1425 | 0.77474 | 19 | 2023-03-10 | 6.86 | 4.2276 | 54.1573 | 21.67 | 54.38 | 166 | - | - | - | 453 | 113 | 6.79 | 2.84
2023-03-11 | 1.7 | 13.33 | 15.03 | 869.5401 | 17.285 | 6.94 | 599.1 | 1061 | 635 | 31.4 | 54 | 7.09 | 658.9 | 1015 | 800 | - | 48000000 | 19000000 | 2023-03-11 | 620 | 6.94 | 800 | 598.9 | 723 | 419 | 6.78 | 17 | 15.9 | 149 | 7770 | 6.79 | 18 | 15.9 | 132 | 15030 | 2023-03-11 | 7.42 | 8.1 | 64 | 8.6 | 3.5 | 19 | 7.2 | 9.1 | 84 | 8.6 | 760 | 190 | 0.5 | 2023-03-11 | 6.88 | 0.92 | 5125 | 3615 | 730 | 141.8856 | 6.835 | 0.515 | 7465 | 4945 | 945 | 127.0362 | 2023-03-11 | 6.4625 | 3.535 | 58.615 | 6.33 | 4.15 | 56.44 | - | 650 | - | 185 | 2023-03-11 | 6.99 | 5.73 | 47.27 | 1092 | 1900 | 0.57474 | 29 | 6.69 | 5.42 | 51.75 | 1400 | 1008 | 1.3889 | 19 | 2023-03-11 | 6.88 | 4.1324 | 49.0291 | 21.02 | 56.33 | 1`72 | - | - | - | 340 | 113 | 6.84 | 3.02
2023-03-12 | 2.2 | 10.7 | 12.9 | 709.8443 | 18.173 | 6.81 | 569.2 | 1052 | 705 | 58.2 | 69 | 7.14 | 719.1 | 1110 | 835 | - | 51000000 | 23000000 | 2023-03-12 | 765 | 7 | 885 | 479.1 | 531 | 369 | 6.79 | 15 | 13.1 | 55 | 8460 | 6.85 | 19 | 16.1 | 57 | 14990 | 2023-03-12 | 7.39 | 6.4 | 26 | 8 | 5.5 | 23.5 | 7 | 8.7 | 118 | 10.8 | 0 | 0 | 0.5 | 2023-03-12 | 6.81 | 0.82 | 5395 | 3845 | 755 | 139.6849 | 6.82 | 0.53 | 7615 | 5400 | 945 | 124.1006 | 2023-03-12 | 6.39 | 3.1425 | 52.3875 | 6.38 | 4.1 | 46.81 | 600 | 525 | 1.1429 | 204 | 2023-03-12 | 7.02 | 4.33 | 45.9 | 972 | 2125 | 0.45741 | 29 | 6.64 | 5.24 | 48.31 | 1356 | 1350 | 1.0044 | 20 | 2023-03-12 | 6.89 | 4.1752 | 46.6951 | 21.66 | 56.84 | 164 | - | - | - | 340 | 170 | 6.74 | 2.97
2023-03-13 | 1.7 | 11.09 | 12.79 | 683.4455 | 18.714 | 7.17 | 539.2 | 1054 | 630 | 54.9 | 67.5 | 7.15 | 749.2 | 1073 | 835 | - | 47000000 | 18000000 | 2023-03-13 | 910 | 6.89 | 1770 | 509.2 | 1042 | 359 | 7 | 17 | 13.2 | 38 | 8830 | 6.96 | 12 | 10.2 | 67 | 16850 | 2023-03-13 | 7.14 | 8.8 | 57 | 11.8 | 6 | 15.4 | 7.05 | 7 | 23 | 8.4 | 230 | 56 | 0.2 | 2023-03-13 | 6.815 | 0.86 | 5210 | 3990 | 835 | 160.2367 | 6.835 | 0.525 | 7175 | 5010 | 955 | 133.1664 | 2023-03-13 | 6.41 | 3.2125 | 61.285 | 6.41 | 4.42 | 60.92 | 624 | 600 | 1.04 | 159 | 2023-03-13 | 7.02 | 4.71 | 51.3 | 1104 | 2150 | 0.51349 | 29 | 6.68 | 4.18 | 55.01 | 1092 | 1550 | 0.70452 | 20 | 2023-03-13 | 6.98 | 4.06 | 53.36 | 22.94 | 52.34 | 154 | - | - | - | - | - | 6.8 | 3.09
2023-03-14 | 2 | 11.86 | 13.86 | 604.5802 | 22.925 | 7.25 | 599 | 1102 | 635 | 48.7 | 46.5 | 7.04 | 569.2 | 1059 | 730 | - | 49000000 | 21000000 | 2023-03-14 | 760 | 7 | 1150 | 479.2 | 1057 | 353 | 7 | 11 | 10.2 | 45 | 9210 | 6.98 | 15 | 11.2 | 60 | 16130 | 2023-03-14 | 7.66 | 9.2 | 55 | 11.4 | 5.5 | 10.9 | 7 | 9.4 | 69 | 11.2 | 440 | 80 | 0.5 | 2023-03-14 | 6.745 | 0.92 | 5755 | 3990 | 890 | 154.7695 | 6.81 | 0.58 | 7165 | 4755 | 925 | 129.7198 | 2023-03-14 | 6.43 | 3.62 | 64.585 | 6.53 | 4.51 | 61.83 | 732 | 525 | 1.3943 | 186 | 2023-03-14 | 7.11 | 4.29 | 53.64 | 1332 | 1500 | 0.888 | 29 | 6.83 | 5.46 | 56.33 | 1308 | 1425 | 0.91789 | 20 | 2023-03-14 | 7.09 | 4.14 | 53.99 | 21.31 | 58.34 | 144 | - | - | - | 453 | 113 | - | -
2023-03-15 | 1.9 | 13.37 | 15.27 | 747.1011 | 20.439 | 7.33 | 630 | 1083 | 780 | 86 | 91.5 | 7.41 | 689 | 1098 | 790 | - | 46000000 | 30000000 | 2023-03-15 | 825 | 7.1 | 1110 | 539 | 1100 | 301 | 7.2 | 15 | 14 | 60 | 9490 | 7.18 | 22 | 16 | 60 | 10960 | 2023-03-15 | 7.48 | 10.2 | 57 | 12.8 | 11 | 30.8 | 7.41 | 9.8 | 57 | 11 | 310 | 20 | 0.2 | 2023-03-15 | 6.675 | 0.92 | 6360 | 3810 | 730 | 114.8228 | 6.77 | 0.575 | 7095 | 4490 | 825 | 116.2576 | 2023-03-15 | 6.6775 | 4.365 | 54.9725 | 6.72 | 4.72 | 50 | - | 425 | - | 126 | 2023-03-15 | 7.21 | 5.6 | 47.11 | - | 1525 | - | 29 | 6.87 | 5.5 | 47.62 | - | 1600 | - | 21 | 2023-03-15 | - | - | - | 21.95 | 58.55 | 97 | - | - | - | 340 | 113 | - | -
2023-03-16 | 1.7 | 13.46 | 15.16 | 818.6629 | 18.518 | 6.96 | 509.3 | 1017 | 670 | 29.7 | 83.5 | 7.24 | 660 | 1042 | 760 | - | 53000000 | 26000000 | 2023-03-16 | 660 | 7.18 | 690 | 480 | 1156 | 386 | 7.17 | 12 | 11 | 43 | 9580 | 7.14 | 11 | 11 | 57 | 11850 | 2023-03-16 | 7.45 | 8.3 | 38 | 9.4 | 6 | 7.3 | 7.29 | 9.6 | 48 | 9.2 | 320 | 210 | 0.2 | 2023-03-16 | 6.745 | 0.7 | 6410 | 3855 | 885 | 138.066 | 6.86 | 0.985 | 7425 | 5353 | 925 | 124.5919 | 2023-03-16 | 6.5625 | 3.5475 | 51.65 | 6.66 | 4.05 | 59.31 | 972 | 500 | 1.944 | 113 | 2023-03-16 | 7.09 | 5.4 | 48.21 | 1356 | 1356 | 1 | 29 | 6.93 | 5.38 | 51.54 | 1164 | 1600 | 0.7275 | 21 | 2023-03-16 | 6.87 | 4.28 | 49.6 | 21.37 | 54.23 | 133 | - | - | - | 453 | 113 | - | -
2023-03-17 | 2.2 | 13.48 | 15.68 | 816.5816 | 19.202 | 7.28 | 479.5 | 1105 | 755 | 24.6 | 51.5 | 7.24 | 569.3 | 1110 | 885 | - | 41000000 | 32000000 | 2023-03-17 | 870 | 7.05 | 1592 | 479.3 | 1134 | 373 | 7.1 | 15 | 13.3 | 38 | 11260 | 7.05 | 18 | 14.3 | 28 | 12530 | 2023-03-17 | 7.22 | 9.7 | 50 | 12.6 | 6.5 | 24.6 | 7.05 | 7.7 | 40 | 9.2 | 340 | 90 | 0.2 | 2023-03-17 | 6.795 | 0.865 | 7195 | 4285 | 940 | 130.7404 | 6.9 | 0.56 | 7725 | 4590 | 930 | 120.5647 | 2023-03-17 | 6.725 | 3.8725 | - | 6.63 | 4.93 | - | - | 575 | - | 103 | 2023-03-17 | 7.19 | 4.04 | - | 1488 | 2075 | 0.71711 | 29 | 6.94 | 4.74 | - | 1392 | 1425 | 0.97684 | 22 | 2023-03-17 | 7.05 | 3.96 | - | 21.13 | - | 141 | - | - | - | 453 | 141 | - | -
2023-03-18 | 1.5 | 13.92 | 15.42 | 913.7236 | 16.876 | 7.21 | 509.1 | 931 | 580 | 62.2 | 44 | 7.2 | 539.5 | 1073 | 605 | - | 53000000 | 49000000 | 2023-03-18 | 530 | 7.11 | 1165 | 449.5 | 943 | 387 | 6.91 | 14 | 12.5 | 38 | 12700 | 6.88 | 12 | 11.5 | 72 | 12770 | 2023-03-18 | 7.33 | 7.7 | 16 | 8.2 | 7.5 | 12.9 | 7.19 | 9.1 | 57 | 11.6 | 180 | 33 | 0.5 | 2023-03-18 | 6.845 | 0.595 | 7090 | 4235 | 960 | 135.4238 | 6.805 | 0.74 | 7975 | 5040 | 950 | 119.1473 | 2023-03-18 | 6.6375 | 3.2625 | 58.9825 | 6.64 | 4.54 | 62.7 | 972 | 550 | 1.7673 | 120 | 2023-03-18 | 7.13 | 3.73 | 52.9 | 1320 | 1900 | 0.69474 | 29 | 6.92 | 4.96 | 53.73 | 1548 | 1750 | 0.88457 | 22 | 2023-03-18 | 7.07 | 4.04 | 56.19 | 21.14 | 56.52 | 173 | - | - | - | 296 | 113 | - | -
2023-03-19 | 1.6 | 13.71 | 15.31 | 858.4726 | 17.834 | 7.44 | 689.1 | 894 | 725 | 69.4 | 67 | 7.34 | 569.1 | 965 | 615 | - | 21000000 | 14000000 | 2023-03-19 | 560 | 7.16 | 880 | 539.1 | 907 | 372 | 7.06 | 20 | 14.7 | 57 | 10430 | 7.03 | 16 | 14.1 | 60 | 11470 | 2023-03-19 | 7.33 | 7 | 40 | 9.4 | 6.5 | 15.7 | 7.33 | 6.6 | 38 | 7.8 | 380 | 0 | 0.5 | 2023-03-19 | 6.88 | 0.645 | 7195 | 4425 | 850 | 118.1742 | 6.85 | 0.815 | 7990 | 5110 | 855 | 107.0289 | 2023-03-19 | 6.6275 | 3.5325 | 56.5375 | 6.71 | 4.67 | 55.33 | 792 | 575 | 1.3774 | 218 | 2023-03-19 | 7.15 | 4.37 | 50.67 | 1344 | 1975 | 0.68051 | 29 | 6.99 | 5.48 | 50.51 | 1332 | 1550 | 0.85935 | 23 | 2023-03-19 | 7.01 | 4.61 | 48.18 | 21.79 | 55.67 | 168 | - | - | - | 566 | 141 | - | -
2023-03-20 | 2 | 13.52 | 15.52 | 710.1025 | 21.856 | 7.08 | 509 | 652 | 520 | 51 | 39.5 | 7.47 | 509.1 | 643 | 515 | - | 53000000 | 21000000 | 2023-03-20 | 595 | 7.24 | 1025 | 569.1 | 1115 | 343 | 7.24 | 13 | 11.7 | 38 | 9450 | 6.82 | 16 | 10.5 | 48 | 11780 | 2023-03-20 | 7.5 | 9.8 | 40 | 9.4 | 5 | 17.6 | 7.12 | 7.4 | 26 | 8.2 | 520 | 210 | 0.2 | 2023-03-20 | 6.805 | 0.7 | 6695 | 4010 | 795 | 118.7832 | 6.88 | 0.74 | 7055 | 4315 | 810 | 114.8572 | 2023-03-20 | 6.59 | 3.4875 | 56.735 | 6.53 | 4.26 | 62.28 | - | - | - | 254 | 2023-03-20 | 7.05 | 5.65 | 46.53 | 1560 | 1825 | 0.85479 | 29 | 6.92 | 4.43 | 52.81 | 1416 | 1600 | 0.885 | 23 | 2023-03-20 | 6.98 | 3.88 | 49.89 | 21.35 | 57.25 | 169 | - | - | - | 283 | 170 | 7.33 | 2.33
2023-03-21 | 2.4 | 11.66 | 14.06 | 601.7805 | 23.364 | 7.22 | 419.1 | 619 | 415 | 77.3 | 69 | 7.33 | 509 | 723 | 535 | - | 29000000 | 1000000 | 2023-03-21 | 460 | 7.08 | 1495 | 479 | 827 | 297 | 7.08 | 15 | 9.8 | 57 | 10060 | - | - | - | - | 11450 | 2023-03-21 | 7.11 | 8.7 | 62 | 9 | 6.5 | 19.6 | 7.29 | 9.8 | 48 | 10.8 | 450 | 120 | 0.2 | 2023-03-21 | 7.055 | 0.745 | 5825 | 3800 | 890 | 153.0775 | 6.795 | 0.775 | 6200 | 3405 | 745 | 120.3582 | 2023-03-21 | 6.63 | 3.31 | 55.4225 | 6.65 | 4.02 | 59.37 | 804 | 375 | - | 162 | 2023-03-21 | 7.02 | 4.02 | 51.97 | 1776 | 2075 | 0.8559 | 29 | 6.94 | 4.54 | 52.54 | 1692 | 1625 | 1.0412 | 24 | 2023-03-21 | 6.96 | 3.75 | 51.3 | 22.1 | 58.65 | 166 | - | - | - | 296 | 170 | 6.63 | 2.38
2023-03-22 | 1.5 | 12.89 | 14.39 | 625.1901 | 23.017 | 7.31 | 389.6 | 940 | 420 | 49.3 | 63.5 | 7.25 | 419.1 | 793 | 430 | - | 54000000 | 27000000 | 2023-03-22 | 515 | 7.11 | 975 | 389.1 | 824 | 339 | 6.89 | 15 | 9.9 | 86 | 10070 | 6.82 | 18 | 10.5 | 98 | 10540 | 2023-03-22 | 7.23 | 7.4 | 23 | 9.8 | 6 | 9.8 | 7.08 | 8.1 | 69 | 9.4 | 670 | 320 | 0.2 | 2023-03-22 | 7.02 | 0.795 | 5885 | 3795 | 925 | 157.1899 | 6.82 | 0.87 | 6055 | 3940 | 875 | 144.5012 | 2023-03-22 | 6.6525 | 3.6 | 56.5775 | 6.62 | 4.28 | 57.09 | 780 | 375 | 2.08 | 222 | 2023-03-22 | 7.01 | 4.26 | 51.93 | 1596 | 1775 | 0.89915 | 29 | 6.93 | 4.48 | 50.97 | 1896 | 1725 | 1.0991 | 25 | 2023-03-22 | 6.94 | 4.31 | 52.9 | 21.18 | 57.49 | 170 | - | - | - | 296 | 141 | 7.45 | 2.24
2023-03-23 | 1.8 | 13.05 | 14.85 | 757.0737 | 19.615 | 7.2 | 539.2 | 902 | 665 | 65.5 | 48 | 7.17 | 599.6 | 885 | 620 | - | 60000000 | 31000000 | 2023-03-23 | 500 | 7.06 | 1065 | 389.6 | 972 | 338 | 6.92 | 13 | 10.4 | 35 | 10690 | 6.89 | 17 | 11 | 35 | 10410 | 2023-03-23 | 7.21 | 11.2 | 23 | 14 | 10.1 | 4.5 | 7.16 | 7.4 | 28 | 8.4 | 640 | 300 | 0.2 | 2023-03-23 | 6.985 | 0.79 | 6225 | 4140 | 945 | 152.3529 | 6.81 | 0.94 | 5465 | 3555 | 730 | 133.2518 | 2023-03-23 | 6.65 | 3.3525 | 51.4375 | 6.68 | 3.72 | 54.14 | 420 | 300 | 1.4 | 136 | 2023-03-23 | 7.06 | 4.17 | 48.57 | 1632 | 1975 | 0.82633 | 29 | 6.96 | 4.71 | 47.14 | 1704 | 1725 | 0.98783 | 26 | 2023-03-23 | 6.98 | 3.91 | 50.1 | 21.14 | 55.98 | 175 | - | - | - | 340 | 141 | 6.56 | 2.35
2023-03-24 | 1.7 | 13.22 | 14.92 | 885.6176 | 16.847 | 7.11 | 449.5 | 897 | 570 | 65.5 | 71.5 | 7.09 | 479.2 | 986 | 565 | - | 55000000 | 28000000 | 2023-03-24 | 660 | 7.06 | 715 | 569.2 | 1136 | 374 | 6.97 | 14 | 12.2 | 33 | 10480 | 6.98 | 21 | 18.2 | 31 | 9810 | 2023-03-24 | 7.18 | 9.7 | 19 | 13.2 | 9 | 12.9 | 7.1 | 10.6 | 23 | 12.6 | 520 | 260 | 0.2 | 2023-03-24 | 6.965 | 0.715 | 6660 | 4670 | 925 | 139.0107 | 6.81 | 0.92 | 5735 | 3735 | 790 | 137.5997 | 2023-03-24 | 6.63 | 3.37 | 57.01 | 6.7 | 4.1 | 58.24 | 672 | 525 | 1.28 | 204 | 2023-03-24 | 7.06 | 4.02 | 49.57 | 1700 | 1476 | 1.1518 | 28 | 6.98 | 4.6 | 50.11 | 1512 | 1650 | 0.91636 | 26 | 2023-03-24 | 6.99 | 3.92 | 53.12 | 21.22 | 55.17 | 169 | - | - | - | 340 | 170 | 6.67 | 2.87
2023-03-25 | 1.5 | 12.13 | 13.63 | 778.9462 | 17.498 | 7 | 539.4 | 744 | 670 | 48.7 | 82 | 7.04 | 569.5 | 998 | 635 | - | 38000000 | 26000000 | 2023-03-25 | 675 | 7 | 980 | 509.5 | 1036 | 303 | 6.95 | 13 | 11.5 | 23 | 8830 | 6.84 | 18 | 14.5 | 33 | 8860 | 2023-03-25 | 7.09 | 11.4 | 28 | 12.4 | 11 | 16.8 | 7.09 | 9.1 | 23 | 13.2 | 460 | 180 | 0.2 | 2023-03-25 | 6.86 | 0.675 | 6750 | 3820 | 925 | 137.6276 | 6.835 | 0.91 | 6045 | 3115 | 805 | 133.1322 | 2023-03-25 | 6.595 | 3.775 | 54.5775 | 6.66 | 4.07 | 58.24 | - | 500 | - | 140 | 2023-03-25 | 7.06 | 4.55 | 49.93 | 1332 | 1775 | 0.75042 | 28 | 6.97 | 4.68 | 49.31 | 1116 | 1525 | 0.7318 | 25 | 2023-03-25 | 6.99 | 3.95 | 54.04 | 21.14 | 56.81 | 171 | - | - | - | - | - | 7.01 | 2.94
2023-03-26 | 1.7 | 15.27 | 16.97 | 861.5525 | 19.697 | 6.9 | 479.5 | 965 | 500 | 73.9 | 51.5 | 7.14 | 599.4 | 1047 | 760 | - | 22000000 | 12000000 | 2023-03-26 | 675 | 6.94 | 1780 | 659.4 | 1078 | 283 | 6.82 | 13 | 11.4 | 48 | 9920 | 6.79 | 15 | 13.4 | 45 | 12510 | 2023-03-26 | 7.25 | 13.3 | 40 | 17.6 | 8 | 9.8 | - | - | - | - | 380 | 60 | 0.5 | 2023-03-26 | 6.81 | 0.65 | 7065 | 4445 | 930 | 132.4551 | 6.765 | 0.82 | 5845 | 3405 | 725 | 124.0494 | 2023-03-26 | 6.58 | 2.95 | 59.1125 | 6.63 | 3.42 | 56.13 | - | 500 | - | 182 | 2023-03-26 | 7.02 | 3.7 | 51.89 | 1440 | 1750 | 0.82286 | 29 | 6.97 | 4.25 | 48.96 | 1128 | 1600 | 0.705 | 26 | 2023-03-26 | 6.98 | 3.4051 | 51.632 | 20.26 | 51.64 | 167 | - | - | - | 453 | 113 | - | -
2023-03-27 | 1.7 | 11.63 | 13.33 | 752.6821 | 17.71 | 6.9 | 479.7 | 756 | 525 | 44.8 | 40.5 | 7.27 | 509.5 | 972 | 690 | - | 42000000 | 31000000 | 2023-03-27 | 605 | 7.25 | 1050 | 569.5 | 1117 | 341 | 7.16 | 19 | 15.5 | 96 | 10960 | 6.71 | 20 | 13.5 | 101 | 9540 | 2023-03-27 | 7.25 | 12.3 | 38 | 16.7 | 8 | 23.5 | 7.18 | 12.7 | 50 | 16.7 | 470 | 190 | 0.5 | 2023-03-27 | 7.005 | 0.6 | 7135 | 4670 | 945 | 132.8704 | 6.75 | 0.805 | 5245 | 3560 | 785 | 149.7459 | 2023-03-27 | 6.7225 | 3.0575 | 55.3175 | 6.71 | 3.56 | 55.74 | 756 | 525 | 1.44 | 171 | 2023-03-27 | 7.4 | 3.82 | 47.94 | 1608 | 1950 | 0.82462 | 29 | 7.27 | 4.44 | 45.89 | 1452 | 1625 | 0.89354 | 26 | 2023-03-27 | 7.27 | 3.7915 | 43.75 | 21.62 | 55.27 | 165 | - | - | - | - | - | 7.25 | 2.4
2023-03-28 | 0.4 | 14.22 | 14.62 | 936.8192 | 15.606 | 7.03 | 479.1 | 969 | 505 | 76.2 | 49.5 | 7.27 | 419.7 | 870 | 460 | - | 51000000 | 19000000 | 2023-03-28 | 410 | 7.25 | 1470 | 509.7 | 919 | 280 | 7.16 | 19 | 12.7 | 84 | 14760 | 6.71 | 15 | 13.7 | 96 | 7050 | 2023-03-28 | 7.19 | 12.3 | 31 | 14 | 6.5 | 10.1 | 7.18 | 11.7 | 33 | 15.3 | 480 | 80 | 0.2 | 2023-03-28 | 6.875 | 0.67 | 7295 | 4695 | 955 | 131.3799 | 6.785 | 0.78 | 4995 | 3389 | 680 | 135.7416 | 2023-03-28 | 6.7025 | 3.6 | 54.1275 | 6.9 | 4.04 | 57.68 | - | 450 | - | 171 | 2023-03-28 | 7.24 | 5.95 | 50.28 | 1440 | 1950 | 0.73846 | 29 | 7.14 | 4.86 | 51.23 | 1344 | 1725 | 0.77913 | 27 | 2023-03-28 | 7.18 | 4.2095 | 53.0945 | 20.55 | 53.31 | 175 | - | - | - | - | - | 7.19 | 2.33
2023-03-29 | 1.9 | 13.34 | 15.24 | 737.6216 | 20.661 | 6.9 | 434.3 | 972 | 590 | 51 | 61 | 7.27 | 569.1 | 972 | 645 | - | 53000000 | 23000000 | 2023-03-29 | 555 | 7.17 | 1300 | 599.1 | 940 | 299 | 7.18 | 15 | 14.1 | 43 | 10430 | 6.71 | 20 | 17.1 | 52 | 9240 | 2023-03-29 | 7.25 | 13.1 | 77 | 18.4 | 6 | 7.6 | 7 | 11.7 | 35 | 12.7 | 620 | 170 | 0.2 | 2023-03-29 | 7.015 | 0.655 | 7140 | 4655 | 950 | 133.7662 | 6.79 | 0.745 | 4890 | 3360 | 650 | 132.7278 | 2023-03-29 | 6.7125 | 3.4825 | 48.61 | 6.69 | 3.75 | 50 | 528 | 450 | 1.1733 | 171 | 2023-03-29 | 7.23 | 4.62 | 45.39 | 1680 | 1900 | 0.88421 | 29 | 7.09 | 4.57 | 44.11 | 1548 | 1625 | 0.95262 | 27 | 2023-03-29 | 7.18 | 3.8895 | 53.6585 | 21.41 | 51.1 | 174 | - | - | - | 481 | 170 | 7.41 | 2.66
2023-03-30 | 1.7 | 14.34 | 16.04 | 799.3223 | 20.067 | 7.07 | 493.9 | 619 | 545 | 61.6 | 49 | 7.37 | 404.3 | 996 | 565 | - | 40000000 | 16000000 | 2023-03-30 | 435 | 7.08 | 620 | 359.3 | 957 | 337 | 7.24 | 19 | 13.7 | 60 | 10190 | 6.92 | 19 | 13.7 | 98 | 8870 | 2023-03-30 | 7.16 | 10.3 | 60 | 12 | 5.5 | 15.7 | - | - | - | - | 590 | 210 | 0.2 | 2023-03-30 | 7.02 | 0.7 | 6945 | 4530 | 935 | 135.2655 | 6.69 | 0.61 | 4755 | 3290 | 650 | 136.5097 | 2023-03-30 | 6.705 | 3.1375 | 61.17 | 6.76 | 4.56 | 54.93 | 852 | 400 | 2.13 | 170 | 2023-03-30 | 7.3 | 3.53 | 50.37 | 1644 | 1850 | 0.88865 | 29 | 7.22 | 4.33 | 49.91 | 1332 | 1675 | 0.79522 | 27 | 2023-03-30 | 7.24 | 3.49 | 52.63 | 20.02 | 53.12 | 174 | - | - | - | - | - | 6.79 | 2.08
2023-03-31 | 1.7 | 14.53 | 16.23 | 932.6514 | 17.402 | 7.27 | 509.1 | 965 | 535 | 66.1 | 57.5 | 7.18 | 508.9 | 793 | 635 | - | 56000000 | 31000000 | 2023-03-31 | 825 | 7 | 905 | 433.9 | 1036 | 329 | 7 | 16 | 12.7 | 57 | 9620 | 6.72 | 13 | 10.9 | 60 | 8870 | 2023-03-31 | 7.22 | 13.5 | 48 | 14.8 | 8 | 14.8 | 6.9 | 10.9 | 57 | 12 | 670 | 320 | 0.2 | 2023-03-31 | 6.62 | 0.66 | 6405 | 4680 | 935 | 147.1 | 6.71 | 0.69 | 4670 | 3870 | 655 | 140.1 | 2023-03-31 | 6.71 | 3.3 | 54.9 | 6.76 | 4.23 | 57.08 | 888 | 500 | 1.776 | 170 | 2023-03-31 | 7.28 | 3.83 | 49.88 | 1128 | 1850 | 0.60973 | 29 | 7.21 | 4.93 | 51.37 | 1104 | 1500 | 0.736 | 27 | 2023-03-31 | 7.48 | 3.6 | 48.8 | 20.38 | 54.48 | 172 | - | - | - | 340 | 141 | 6.59 | 2.31
AVG | 1.7935 | 12.7329 | 14.5265 | 758.8924 | 19.3693 | 7.071 | 544.3433 | 933.1935 | 637.0968 | 50.4452 | 62.1129 | 7.166 | 576.85 | 980.1667 | 693.1667 |  | 53322580.6452 | 22290322.5806 | AVG | 686.5 | 7.044 | 1244.2333 | 525.85 | 945.6333 | 337.0323 | 6.9877 | 15.8667 | 13.01 | 59.7 | 9958.2 | 6.8855 | 17.5172 | 13.6862 | 70.6552 | 12383.6667 | AVG | 7.2435 | 9.3867 | 47.1613 | 11.2742 | 6.6484 | 14.1065 | 7.1304 | 8.9 | 48.1071 | 10.4429 | 440.6452 | 144.4839 | 0.31613 | AVG | 6.8222 | 0.7595 | 6289.3333 | 4056.2069 | 860 | 137.6049 | 6.7713 | 0.709 | 6722.6667 | 4313.8621 | 847.3333 | 127.1744 | AVG | 6.5747 | 3.5305 | 57.6875 | 6.5729 | 4.4306 | 57.511 | 701.1429 | 493.5185 | 1.436 | 159.5161 | AVG | 7.0728 | 4.4424 | 50.1932 | 1360.5714 | 1833 | 0.74618 | 28.931 | 6.8831 | 4.991 | 51.3529 | 1301 | 1512.3448 | 0.86574 | 22.3793 | AVG | 6.9946 | 4.0293 | 51.4447 | 21.4746 | 55.3615 | 159.8333 |  |  |  | 396.84 | 143.64 | 6.8713 | 2.8117
Remarks: | [18 empty] | Remarks: | [30 empty] | Remarks: | [12 empty] | Remarks: | [10 empty] | Remarks: | [14 empty] | Remarks:
*BDL - Below Detectable Limit, ([-] - analysis not conducted) | [18 empty] | *BDL - Below Detectable Limit | [16 empty] | *BDL - Below Detectable Limit | [13 empty] | *BDL - Below Detectable Limit | [12 empty] | *BDL - Below Detectable Limit | [10 empty] | *BDL - Below Detectable Limit | [14 empty] | *BDL - Below Detectable Limit
VA TECH WABAG | [14 empty] | PID | KVWSMB |  |  | VA TECH WABAG | [7 empty] | PID |  |  |  |  | KVWSMB |  |  |  | VA TECH WABAG | [9 empty] | PID | KVWSMB |  |  | VA TECH WABAG |  |  |  |  | PID |  |  |  | KVWSMB |  |  |  | VA TECH WABAG |  |  |  |  | PID |  |  | KVWSMB |  |  | VA TECH WABAG |  |  |  |  | PID |  |  |  |  | KVWSMB |  |  |  |  | VA TECH WABAG | [9 empty] | PID |  | KVWSMB
CHEMIST |  |  |  |  | PLANT INCHARGE | [6 empty] | PLANT INCHARGE | [6 empty] | CHEMIST |  | PLANT INCHARGE | [14 empty] | CHEMIST | [7 empty] | PLANT INCHARGE | [5 empty] | CHEMIST |  | PLANT INCHARGE | [10 empty] | CHEMIST |  | PLANT INCHARGE | [8 empty] | CHEMIST |  | PLANT INCHARGE | [12 empty] | CHEMIST |  |  | PLANT INCHARGE
Formulas:
Date = [Date]
Aeration Tank = [Date]
Digester Sludge Feeding Details = [Aeration Tank]
Digester Performance Details = [Digester Sludge Feeding Details]
Digester Outlet = [Digester Performance Details]